       [image: image1.jpg]



the hashemite kingdom of jordan
the jordanian electric power company limited

Specification JEP 7/2026

tender document for

OUTDOOR Heatshrinkable breakouts & insulating tubes for low voltage cables
	Tenderer's Name:
	____________________

	Address:

	____________________
____________________

	Closing Date:
	____________________

	Closing Time:
	____________________


january   2026
THE JORDANIAN ELECTRIC POWER COMPANY LIMITED

AMMAN  –  JORDAN

	Telephone 962 6 4648411

P.O. BOX 618

ZIP CODE 11118
	____________
	CABLE: ELECTRICO

FAX 962 6 5503618


SPECIFICaTION  JEp 7/2026
OUTDOOR HEATSHRINKABLE BREAKOUTS & INSULATING TUBES FOR LOW VOLTAGE CABLES
SCOPE OF WORK
The works shall comprise the design, manufacture, works testing, supply and delivery to Aqaba port, The Hashemite Kingdom of Jordan of the following:
	ITEM NO.
	Equipment
	Quantity

	1.
	Heat shrinkable, UV resistance, low voltage cable breakouts suitable for 4X(10-35mm2), 600/1000 V, 4 ways cable with 40/15mm body range and 15/3mm fingers range.
	40,000
Each

	2.
	Heat shrinkable, UV resistance, low voltage cable breakouts suitable for 4X(50-120mm2), 600/1000 V, 4 ways cable with 72/25mm body range and 25/9mm fingers range.
	3,000
Each

	3.
	Heat shrinkable, UV resistance, low voltage cable breakouts suitable for 4X(150-240mm2), 600/1000 V, 4 ways cable with 90/35mm body range and 34/12mm fingers range.
	4,000
Each

	4.
	Heat shrinkable, UV resistance, low voltage cable breakouts suitable for 3X(50-120mm2), 600/1000 V, 3 ways cable with 72/25mm body range and 25/9mm fingers range.
	1,000

Each

	5.
	Heat shrinkable, UV resistance, low voltage cable breakouts suitable for 2X(10-35mm2), 600/1000 V, 2 ways cable with 40/15mm body range and 15/3mm fingers range.
	50,000

Each

	6.
	Heat shrinkable, with adhesive, colored*, UV resistance protection tubes for low voltage cables 4x(10-35mm2), 600/1000V, with range of 15/3mm, Min. thickness shall be 1.8mm.

The total quantity shall be separated to four forth: 25% red, 25% yellow, 25% blue and 25% black.
	60,000

Meters

	7.
	Heat shrinkable, with adhesive, colored*, UV resistance protection tubes for low voltage cables 4x(50-120mm2), 600/1000V, with range of 25/9mm, Min. thickness shall be 1.8mm.

The total quantity shall be separated to four forth: 25% red, 25% yellow, 25% blue and 25% black.
	12,000

Meters

	8.
	Heat shrinkable, with adhesive, colored*, UV resistance protection tubes for low voltage cables 4X(150-240mm2), 600/1000V, with range of 34/12mm, Min. thickness shall be 1.8mm.

The total quantity shall be separated to four forth: 25% red, 25% yellow, 25% blue and 25% black.
	6,000

Meters

	9.
	Heat shrinkable, with adhesive, only black colored, UV resistance protection tubes for low voltage cables as an outer jacket, 600/1000V, with range of 85/29mm, Min. thickness shall be 2.5mm.
	1,000

Meters

	10.
	Heat shrinkable, with adhesive, only black black colored, UV resistance protection tubes for low voltage cables, 600/1000V, with range of 115/37mm, Min. thickness shall be 2.5mm.
	1,000

Meters


*Black tubes (not colored if submitted) could be accepted subject to the approval by the Engineer.
Notes:

1. Above tubes shall be packed in rolls as suitable, Kitting length shall be specified at stage of award.
2. Documents to be submitted as an integral part of the offer, and to be evaluated with the tender:

a. Full technical details, drawings and catalogues.

b. Fully detailed reference list with contact details.
c. Complete Test certificates including UV proof from reputable well recognized third party      laboratory to ensure that the breakouts and tubes comply with the requirements of this specification.
d. ISO certificate and any other documents that may assist in the evaluation.
3. Minor deviations could be considered and subjected to the approval by the Engineer.
4. Two identical non-returnable representative samples for each item shall be provided with the offer, to be thoroughly examined for technical compliance. Failure of the sample or failure to provide samples may entitle JEPCO to consider the offer non-responsive.

5. JEPCO has the right to award the quantity of this Tender in two equal shipments (within six to nine months apart).

Schedule A2 

Summary Schedule

Technical and Commercial Data

Note: The following schedule represents the most essential data based on which the evaluation process shall be performed.
	item
	Description
	Quantity
	Manufacturer/

Origin
	Colored or black
	Model/ size
	Unit CFR to Aqaba Port Price/ Currency
	Total CFR to Aqaba Port Price/ Currency
	Delivery

(Weeks)

	1.
	Heat shrinkable, UV resistance, low voltage cable breakouts suitable for 4X(10-35mm2), 600/1000 V, 4 ways cable with 40/15mm body range and 15/3mm fingers range.
	40,000

Each
	
	
	
	
	
	

	2.
	Heat shrinkable, UV resistance, low voltage cable breakouts suitable for 4X(50-120mm2), 600/1000 V, 4 ways cable with 72/25mm body range and 25/9mm fingers range.
	3,000

Each
	
	
	
	
	
	

	3.
	Heat shrinkable, UV resistance, low voltage cable breakouts suitable for 4X(150-240mm2), 600/1000 V, 4 ways cable with 90/35mm body range and 34/12mm fingers range.
	4,000

Each
	
	
	
	
	
	

	4.
	Heat shrinkable, UV resistance, low voltage cable breakouts suitable for 3X(50-120mm2), 600/1000 V, 3 ways cable with 72/25mm body range and 25/9mm fingers range.
	1,000

Each
	
	
	
	
	
	

	5.
	Heat shrinkable, UV resistance, low voltage cable breakouts suitable for 2X(10-35mm2), 600/1000 V, 2 ways cable with 40/15mm body range and 15/3mm fingers range.
	50,000

Each
	
	
	
	
	
	

	6.
	Heat shrinkable, with adhesive, colored*, UV resistance protection tubes for low voltage cables 4x(10-35mm2), 600/1000V, with range of 15/3mm, Min. thickness shall be 1.8mm.

The total quantity shall be separated to four forth: 25% red, 25% yellow, 25% blue and 25% black.
	60,000

Meters
	
	
	
	
	
	

	7.
	Heat shrinkable, with adhesive, colored*, UV resistance protection tubes for low voltage cables 4x(50-120mm2), 600/1000V, with range of 25/9mm, Min. thickness shall be 1.8mm.

The total quantity shall be separated to four forth: 25% red, 25% yellow, 25% blue and 25% black.
	12,000

Meters
	
	
	
	
	
	

	8.
	Heat shrinkable, with adhesive, colored*, UV resistance protection tubes for low voltage cables 4X(150-240mm2), 600/1000V, with range of 34/12mm, Min. thickness shall be 1.8mm.

The total quantity shall be separated to four forth: 25% red, 25% yellow, 25% blue and 25% black.
	6,000

Meters
	
	
	
	
	
	

	9.
	Heat shrinkable, with adhesive, only black colored, UV resistance protection tubes for low voltage cables as an outer jacket, 600/1000V, with range of 85/29mm, Min. thickness shall be 2.5mm.
	1,000

Meters
	
	
	
	
	
	

	10.
	Heat shrinkable, with adhesive, only black black colored, UV resistance protection tubes for low voltage cables, 600/1000V, with range of 115/37mm, Min. thickness shall be 2.5mm.
	1,000

Meters
	
	
	
	
	
	


3

