[image: image4.wmf]ú

û

ù

+

ê

ë

é

500

500

2

1

L

L


t
Photograph 1
the hashemite kingdom of jordan
the jordanian electric power company limited

Specification JEP 17/2026

tender document for

11 & 33 kV WTR-XLPE INSULATED CABLEs
 
form of tender
technical specification
schedules


	Tenderer's Name:
	____________________

	Address:
	____________________

	Closing Date:
	____________________

	Closing Time:
	____________________


JANuary 2026

TABLE OF CONTENTS
61.
scope of work


61.1
Definite work


72.
sITE AND DESIGN PARTICULARS


72.1
Particulars of system


72.2
Electrical design data


72.2.1
System particulars


72.2.2
Equipment withstand voltage


82.2.3
Outdoor bushing and insulator creepage distances


82.2.4
Cable box clearances


82.2.5
Minimum clearance from live metal to oil pipe work


92.2.6
Auxiliary power supplies


92.3
Site conditions


92.3.1
General


92.3.2
Elevation


92.3.3
Earthquakes


92.3.4
Snow


92.3.5
Hail


102.3.6
Air temperature (Degrees Centigrade)


102.3.7
Rainfall amount (millimetre)


102.3.8
Relative humidity (%)


102.3.9
Mean wind speed (m/s)


112.3.10
Clouds “oktas”


112.3.11
Fog “visibility 1 km or less”


112.3.12
Dust “visibility 1 km or less”


112.3.13
Thunderstorms


123.
GENERAL TECHNICAL CLAUSES


123.1
Standards


123.2
Design and standardization


133.3
Galvanizing


143.4
Copper conductors


143.5
Aluminium and aluminium alloys


143.6
Labels and identification plates


163.7
Bolts and nuts


163.8
Cleaning and painting


173.8.1
External surfaces at works


173.8.2
Internal surfaces


173.9
Insulating oil and gas


183.10
Prevention of acidity


183.11
Fire precautions


183.12
Corona and radio interference


183.13
Locking devices and padlocks


183.14
Tools


183.15
Erection marks


193.16
Operating and maintenance instructions


193.17
Spare parts


193.18
Manufacturing experience and qualifications


193.19
Quality Assurance system


204
11& 33 KV XLPE INSULATED CABLES


204.1
GENERAL REQUIREMENTS


204.2
Rated Voltage


204.3
CONDUCTOR


204.4
INSULATION AND SCREENING


204.4.1
CONDUCTOR SCREEN


204.4.2
XLPE INSULATION


214.4.3
INSULATION SCREEN


214.4.4
METALLIC SCREEN


214.4.5
LONGTUDINAL WATERTIGHTNESS LAYERS


214.4.6
OUTER SHEATH


224.5
SEALING AND DRUMMING


235.
MULTIPAIR THERMOPLASTIC INSULATED CABLES


235.1
General


235.2
Conductors


235.3
Thermoplastic Insulation


235.4
Core Identification


235.5
Twinning and Laying-Up


245.6
Inner Sheath


245.7
Wire Armour


245.8
Oversheaths


245.9
Sealing and Drumming


245.10
Testing


256
WORKS TESTS FOR CABLES


256.1
General Requirements


256.2
Galvanising


256.3
XLPE Insulated Power Cables


256.3.1
Type Tests (Electrical and Non-electrical)


266.3.2
Routine Tests


266.3.3
Ageing Test


266.3.4
Special Tests


266.4
Polyethylene Insulated Multipair Cables


266.4.1
Routine Tests on Completed Cable


286.4.2
Sample Tests


286.4.3
Galvanising


Error! Bookmark not defined.SCHEDULE a


30SCHEDULE B


31SCHEDULE C


32SCHEDULE D


44SCHEDULE e


46sCHEDULE f1


47sCHEDULE f2


49schedule K


50schedule n





LIST OF ABBREVIATIONS

	BS
	British Standards

	IEC
	International Electrotechnical Commission

	JEPCO
	The Jordanian Electric Power Company Limited


Form oF Tender
THE JORDANIAN ELECTRIC power COMPANY LIMITED
TENDER FOR CONTRACT NO JEP 17/2026

11 & 33 kV WTR-XLPE INSULATED CABLEs
 (Tenderers are required to fill up the blank spaces in this Tender Form and Appendix)

The General Manager

The Jordanian Electric Power Company Limited

P.O. Box 618

Amman 11118

The Hashemite Kingdom of Jordan

1.
Having examined the Drawings, Conditions of Contract, Specification and Schedules for the execution of the above-named Goods, we, the undersigned, offer to execute, complete and remedy defects in the whole of the said Goods in conformity with the said Drawings, Conditions of Contact, Specification and Schedules for the sum of 




(Figures…………..………………….)
or such other sum as may be determined in accordance with the said conditions.

2.
We agree to abide by this Tender for the period of 120 days from the date fixed for receiving the same and it shall remain binding upon us and may be accepted at any time before the expiration of that period.  

3.
We undertake if our Tender is accepted to complete and deliver the whole of the Goods comprised in the Contract within 
…………… week(s) subject to the said Conditions.

4.
If our Tender is accepted we will obtain the guarantee of an Insurance Company or Bank or other sureties (to be approved by you) to be jointly and severally bound with us in a sum not exceeding 10 per cent of the above named sum for the due performance of the Contract under the terms of a Bond to be approved by you.  

We propose the following Bank or Insurance Company as surety (or sureties) in this respect:

(
)

(
)

(
)

5.
Unless and until a formal Agreement is prepared and executed, this Tender, together with your written acceptance thereof, shall constitute a binding Contract between us.

6.
We undertake to provide a defects guarantee period as stated in Clause 15 of the conditions of contract for each section of the Plant from the date of delivery to the Port of Aqaba, or such other destination that may be stated in the Contract.  

7.
We understand that you are not bound to accept the lowest or any Tender you may receive.

8.
Tenderers must give details of their representative or associated companies in the Hashemite Kingdom of Jordan who will deal with this Contract if it is awarded to the Tenderer:

Name and Full Address of Representative:




Telephone Number



Fax Number



9.
APPENDIX TO TENDER

	
	Clause
	

	Time for completion
	10.1
	
 weeks

	Amount of Bond or Guarantee
	 7.1
	10% of Contract sum 


	
	11.1
	Full replacement value +
 10%

	Amount of reduction per week of delay
	23.1
	1% 

 of Contract Price

	Maximum reduction
	23.1
	10% 

of Contract Price

	Defects Liability Period
	15.2
	


	Use of Goods assumed
	
	

24 hours per day

	Name and address of Tenderer’s Bank
	
	



Dated this 

day of 


20…

Signature 

in the capacity of 


duly authorized to sign tenders for and on behalf of 


Witness

Address


Occupation

1.
scope of work

1.1
Definite work

The works shall comprise the design, manufacture, testing and delivery to the Port of Aqaba, The Hashemite Kingdom of Jordan of the equipment listed in this Specification, equipment in accordance with the Conditions of Contract at prices stated in the Schedule of this Specification, together with the provision of certain specified spares.  
	Item No.
	Description
	Quantity
(km)

	1.
	8.7/15 kV, 120 mm2 Al., 1-CORE, WTR-XLPE CABLE
	10

	2.
	8.7/15 kV, 240 mm2 Al., 1-CORE, WTR-XLPE CABLE
	50

	3.
	8.7/15 kV, 400 mm2 Al., 1-CORE, WTR-XLPE CABLE
	600

	4.
	19/33 kV, 300 mm2 Al., 1-CORE, WTR-XLPE CABLE
	60

	5.
	19/33 kV, 500 mm2 Al., 1-CORE, WTR-XLPE CABLE
	300

	6.
	19/33 kV, 70 mm2 Al., 1-CORE, WTR-XLPE CABLE
	Not Required


Notes

· Documents to be submitted as an integral part of the offer, and to be evaluated with the tender:

1. Full technical details, drawings and catalogues.

2. Type test certificates from any European STL member laboratory (KEMA, CESI, and IPH) or equivalent.

3. Fully detailed reference list with contact details.

4. ISO certificate and any other documents that may assist in the evaluation.

· Drum capacity shall be 1000 ± 2% m for 1-core cables.
· The wooden drums shall be returned after being unloaded by JEPCO, the manufacturer shall be responsible of taking the drums after notifying him from our side and no later than two weeks.

· The above items shall be provided with a bar code of 128 type C that represents the primary and secondary number of these items, as shown in the table below:
	Item No.
	Item Code

	1.
	00090103

	2.
	00260103

	3.
	00270103

	4.
	00070101

	5.
	00080101

	6.
	0050101


2.
sITE AND DESIGN PARTICULARS

2.1
Particulars of system
The following are the particulars of the systems on which the equipment covered by the Specification shall operate:-
i.       33 kV 3-phase at a frequency of 50 Hz with the neutral point resistance earthed.  

ii.
11 kV 3-phase at a frequency of 50 Hz with the neutral point solidly earthed.  

iii.    415 volts 3-phase and neutral at a frequency of 50 Hz with the neutral point solidly earthed.  

2.2
Electrical design data
2.2.1
System particulars
	Nominal system voltage between phases
	
kV
	
33
	
11
	
0.415

	Highest system voltage
	kV
	36
	12
	0.440

	System fault level
	kA
	25
	25
	50*

	Earthing system
	

	Resistance earthed
	Solidly
earthed
	Solidly
earthed

	System frequency
	Hz
	50
	50
	50


2.2.2
Equipment withstand voltage
	i.

	Outdoor bushings, insulators and pole mounted transformers

	
	Impulse withstand voltage (1.2/50µs wave) peak
	
kV
	
250
	
95
	
-

	
	Power frequency withstand voltage
	
kV
	
95
	
38
	
-

	ii.

	All other equipment excluding pole mounted transformers

	
	Impulse withstand voltage (1.2/50µs wave) peak
	
kV
	
170
	
75
	
-

	
	Power frequency withstand voltage
	
kV
	
75
	
28
	
-


2.2.3
Outdoor bushing and insulator creepage distances
	Minimum creepage distance
	mm
	1116
	372
	-

	Protected creepage distance
	Not to exceed 50% of creepage distance


2.2.4
Cable box clearances
The minimum cable box clearances under compound or oil shall be as follows:-

	Nominal system voltage
	kV
	33
	11
	Below 1

	Minimum clearance between phases
	
mm
	
125
	
45
	
20

	Minimum clearance phase to earth
	
mm
	
100
	
32
	
20

	Minimum creepage distance phase to earth over cable surface
	

mm
	

250
	

125
	

26

	The minimum cable box clearances in air-filed, air-insulated boxes, live metal to live metal and unshrouded shall be as follows:-

	Nominal system voltage
	kV
	33
	11
	

	Minimum clearance between phases
	
mm
	
430
	
250
	

	Minimum clearance phase to earth
	
mm
	
320
	
150
	

	Minimum creepage distance phase to earth over cable tail surface
	

mm
	

800
	

450
	

	The minimum cable box clearance in air-filled boxes with shrouded insulation termination is as follows:-

When this type of termination is used the dimensions will be based on the termination manufacturers recommendations and be subject to approval by the Engineer.  


2.2.5
Minimum clearance from live metal to oil pipe work (including conservator and pressure relief devices on transformers)

	Highest system voltage
	kV
	36
	12

	Minimum clearance
	mm
	485
	250

	Apart from the clearances detailed under this item, no phase or earth clearances are specified for transformers where an impulse voltage test level is specified.  


2.2.6
Auxiliary power supplies
	Supply voltage for auxiliary equipment
	i.
400 volt, 3 phase and Neutral 50 Hz

	
	ii.
110 volts DC 2 wire


2.3
Site conditions

2.3.1
General
The site conditions shall be assumed to be as follows for the purposes of Tender preparation.  

2.3.2
Elevation
766 meters above sea level - Amman Airport at which all the climatic observations used were taken by the Jordanian Ministry of Transport Meteorological Department.  

2.3.3
Earthquakes
Amman is classified as Seismic Zone 2.  

2.3.4
Snow
Snowfall in cm at Locations in the Amman Area in 10 years 1972-1982.  

	Area
	No of days of snowfall/year
	Greatest depth of snow (cm)

	Wadi Dhuleil
	1-04
	10

	Amman Airport
	1-13
	30

	Jordan University
	1-13
	60

	Naur
	1-13
	45

	Madaba
	1-04
	25


2.3.5
Hail
Not a normal occurrence but occurs on average 3.2 days per year.  

	Station: Amman Airport
	31 deg 59 min NORTH
35 deg 59 min EAST
766 m above sea 

	Period: 1923 - 1985
	


2.3.6
Air temperature (Degrees Centigrade)

	
	JAN
	FEB
	MAR
	APR
	MAY
	JUN
	JUL
	AUG
	SEP
	OCT
	NOV
	DEC
	YEAR-LY

	Mean monthly
	
7.9
	
9.
	
11.7
	
15.9
	
20.5
	
23.6
	
25.1
	
25.4
	
23.5
	
20.4
	
14.9
	
9.8
	
17.3

	Mean daily max
	
12.4
	
13.8
	
17.4
	
22.5
	
27.8
	
30.9
	
31.9
	
32.4
	
30.7
	
27.2
	
20.6
	
14.5
	
23.5

	Mean daily min
	
3.5
	
4.2
	
6.1
	
9.3
	
13.3
	
16.3
	
18.2
	
18.3
	
16.2
	
13.6
	
9.3
	
5.1
	
11.1

	Absolute max
	26.3
	29.4
	32.5
	39.2
	40.6
	42.8
	42.4
	42.8
	40.6
	37.4
	.8
	27.3
	42.8

	Absolute min
	-7.5
	-6.5
	-3.9
	0.0
	3.0
	7.8
	11.0
	11.5
	8.9
	4.9
	-3.2
	-5.3
	-7.5

	Design ambient temperature is 45 degrees centigrade


2.3.7
Rainfall amount (millimetre)

	Mean monthly
	
64.5
	
63.9
	
44.7
	
16.1
	
3.7
	
0.03
	
TR
	
TR
	
0.4
	
5.8
	
28.6
	
48.6
	
276.3

	Max amount in a month
	

235.2
	

190.8
	

168.7
	

151.3
	

30.6
	

1.1
	

TR
	

TR
	

15.4
	

54.6
	

136.8
	

179.8
	

476.5

	Max amount in one day
	

75.6
	

80.0
	

66.2
	

52.4
	

24.1
	

1.1
	

TR
	

TR
	

15.4
	

40.5
	

79.4
	

73.6
	

80.0


2.3.8
Relative humidity (%)

	Mean monthly
	
70.0
	
67.0
	
60.0
	
50.0
	
39.0
	
37.0
	
40.0
	
43.0
	
47.0
	
46.0
	
56.0
	
68.0
	
52.0

	Max relative humidity reaches 100 per cent especially during rainy intervals and night, while min relative humidity drops to less than 10 per cent on some occasions especially during Khamsinic conditions (22 March - 10 May).  


2.3.9
Mean wind speed (m/s)

	Direction (deg)
	
227
	
241
	
251
	
254
	
275
	
276
	
278
	
282
	
284
	
267
	
226
	
222
	
264

	Mean monthly
	
3.2
	
3.3
	
3.4
	
3.6
	
3.3
	
3.6
	
3.9
	
3.4
	
2.6
	
2.2
	
2.4
	
2.9
	
3.2

	Max wind gust
	

35
	

28
	

30
	

31
	

24
	

22
	

19
	

17
	

17
	

26
	

26
	

34
	

…..


2.3.10
Clouds “oktas”

	Mean amount
	
3.8
	
3.5
	
3.4
	
3.2
	
1.9
	
0.6
	
0.3
	
0.3
	
0.7
	
1.5
	
2.6
	
3.4
	
2.1

	No cloudy days
	

4.7
	

3.1
	

3.8
	

2.5
	

0.7
	

0.0
	

0.0
	

0.0
	

0.0
	

0.3
	

1.0
	

3.6
	

19.5


2.3.11
Fog “visibility 1 km or less”

	Mean no of days
	
1.5
	
0.7
	
0.4
	
0.2
	
0.0
	
0.0
	
0.0
	
0.0
	
0.0
	
0.1
	
0.3
	
0.7
	
3.9

	Max number of days with fog 11 days per year


2.3.12
Dust “visibility 1 km or less”

	Mean no of days
	
0.4
	
0.1
	
0.6
	
0.2
	
0.2
	
0.0
	
0.0
	
0.0
	
0.0
	
0.0
	
0.2
	
0.1
	
1.7

	Max number of days with dust 6 days per year


2.3.13
Thunderstorms

	Mean no of days
	
0.4
	
0.4
	
1.3
	
0.8
	
0.6
	
0.0
	
0.0
	
0.0
	
0.4
	
1.2
	
1.1
	
0.4
	
6.6

	Max number of days with thunder storms 17 days per year


3.
GENERAL TECHNICAL CLAUSES

3.1
Standards

Although IEC standards for workmanship, material and equipment have been selected in these specifications as a basis of reference, standards and specifications of EC member countries and recommendations of standard international organisations will be acceptable provided they are substantially equivalent or higher than the designated standards and provided furthermore that the Supplier submits for approval detailed specifications which he proposes to use. Furthermore, certain special requirements are detailed herein that overrule any other standards and shall be met during manufacturing/testing.

When IEC recommendations or national standards are referred to the Edition shall be that current at the date of Tender, together with any amendments issued to that date.  

If requested by the Engineer, the Contractor shall supply at his own expense three copies in English and one in the original language of any national standards which are applicable to the Contract.  

3.2
Design and standardization

The goods shall be designed to facilitate inspection, cleaning and repairs, and for operation in which continuity of service is the first consideration. All apparatus shall be designed to ensure satisfactory operation under the atmospheric conditions prevailing at the Sites and under such sudden variations of load and voltage as may be met with under working conditions on the system, and short circuits, including those due to faulty synchronising within the rating of the apparatus.

The design shall incorporate every reasonable precaution and provision for the safety of all those concerned in the operation and maintenance of the Goods and of associated works supplied under other Contracts.

All material used shall be of the best quality and of the class most suitable for working under the conditions specified and shall withstand the variations of temperature and atmospheric conditions arising under working conditions without distortion or deterioration or the setting up undue stresses in any part, and also without affecting the strength and suitability of the various parts for the work which they have to perform. No welding, filling or plugging of defective parts will be permitted without the sanction in writing of the Engineer.

Corresponding parts liable to renewal shall be interchangeable. When required by the Engineer, the Supplier shall demonstrate this quality.

All apparatus shall operate without undue vibration and with the least practicable amount of noise. 

Cast iron shall not be used for chambers of oil-filled apparatus or for any part of the equipment which is in tension or subject to impact stresses except where it can be shown that service experience has been satisfactory with the grade of cast iron and the duty proposed.

Operating boxes, kiosks, cubicles and similar enclosed compartments forming part of auxiliary equipment shall be adequately ventilated to restrict condensation, and, where required by the Engineer, suitable low-temperature heaters shall be provided. All contactor or relay coils and other parts shall be suitably protected against corrosion.

All outdoor apparatus, including bushing insulators and fittings shall be so designed as to avoid pockets in which water can collect.

The underside of all tanks shall be ventilated in an approved manner to prevent corrosion.

Accessible means shall be provided for the easy lubrication of all bearings and where necessary, of any mechanism or moving part. Grease lubricators shall be fitted with hexagon nipples.

All mechanisms shall, when necessary, be constructed of stainless steel, brass or gunmetal to prevent sticking due to rust or corrosion.

              All taper pins used in any mechanism shall be of the split type.

The busbars, connections, isolators, fuses, contacts, cable boxes, trunking connections etc,. which form part of the Contract Works shall not exceed the temperature rise values specified in the relevant IEC publication or equivalent national standard. 

All connections and contacts shall be of ample section and surface for carrying continuously the specified currents without undue heating, and shall be secured by bolts or set screws of ample size, fitted with locking devices of approved type and material.

All rubbing or wearing surfaces shall be machine surfaced. Joints employing a gasket material shall be so constructed that the packing is maintained under sufficient compression in all parts, so that an efficient joint can be made without the use of jointing compounds.  Gasket material shall be of the minimum thickness necessary and of approved composition.

All apparatus shall be designed to obviate the risk of accidental short circuit due to animals, birds, and vermin. Openings in ventilated enclosures shall be so constructed to prevent the entry of vermin and insects.

3.3
Galvanizing

Galvanizing shall be applied by the hot dipped process.  The preparation for galvanizing and the galvanizing process shall not adversely affect the mechanical properties of the material being coated.  The zinc coating shall be clean, of uniform thickness and free from defects.  

When zinc spray coating is used, surfaces shall be shot blasted before spraying.  

Drilling, punching, cutting, bending and removal of burrs shall be completed before galvanizing/zinc spray coating.  

The average thickness of the zinc coating shall be equivalent to not less than 0.6 kg/m2 of zinc for all surfaces, except steel wires.  

The thickness of the zinc coating for steel wires shall be in accordance with a national standard and shall be approved by the Engineer.  

Material on which galvanizing has been damaged shall be re-dipped unless, in the opinion of the Engineer, the damage is local and can be repaired by applying a coat of galvanizing repair paint.  Where such a repair is authorized, the damaged area shall be cleaned by wiping with clean rags saturated with mineral spirits or xylene followed by wire brushing.  After wire brushing, the area shall be re-cleaned with solvent to remove residue and shall be given a minimum of two coats of zinc rich paint in accordance with the manufacturer’s instructions.  

Samples selected by the Engineer of all galvanized material shall be subjected to the galvanizing tests set out in the appropriate material standard (eg BS 443/BS 729).  

Sheradizing or other similar processes shall not be used unless expressly approved by the Engineer.  

Surfaces in contact with oil shall not be galvanized or cadmium plated.  

3.4
Copper conductors

All copper conductors shall be composed of high conductivity electrolytic copper having a conductivity of not less than 99.9 per cent of the International Agreed Copper Standard (IACS).  

3.5
Aluminium and aluminium alloys

Aluminium shall be of high commercial quality. The composition, including the percentage and nature of any impurities, shall be stated in the schedules.  

All aluminium alloys shall be of approved compositions as stated in the schedules.  

Aluminium and aluminium alloy castings shall be sound and free from porosity.  

3.6
Labels and identification plates

All equipment shall be clearly and permanently labelled, to the approval of the Engineer, in English, unless otherwise specified.  Where labels are provided in diagrammatic form, any inscription shall be in English unless otherwise specified.  

A label shall be permanently fixed to each item of equipment in a clearly visible position stating:  

Property of The Jordanian Electric Power Co Ltd
Year of Manufacture

All control and relay panels, marshalling boxes, kiosks, distribution boxes and other cubicles shall be labelled to show the circuit with which it is associated.  These labels shall be fitted to the front and back of all equipment.  

Labels, number plates and their fixing screws, for outdoor use, shall be of stainless steel or other corrosion resistant material.  Where the use of vitreous enamelled labels is approved, the whole surface including the back and edges shall be properly covered and protective washers shall be provided front and back on the fixing screws.  

The materials of the labels and number plates, for indoor and outdoor use, shall be approved by the Engineer and shall be fixed so as to prevent buckling due to temperature and humidity variations.  

Danger notices shall have red lettering on a white background and shall be in English and Arabic.  

Unless otherwise approved by the Engineer, all other labels and number plates shall have black inscriptions on a white base colour.  

Labels for similar equipment shall be of uniform appearance and the dimensions and size of letter shall be to the approval of the Engineer.  
Each equipment shall be marked with its function, manufacturer's name or trade mark and the code type number together with the batch or serial number.
Each detachable unit shall be either marked so as to enable it to be identified with the parent equipment, or else marked with the manufacturer's name and type number or code number and where definable, its function.

Each Unit and sub-unit mounting position shall be marked to indicate the type of unit or sub-unit to be located in that position. Add markings may be required for apparently identical units or sub-units having different pre-set characteristics.

Component reference numbers shall be marked adjacent to the component. Where this is impossible, components shall be identifiable from the drawings provided by the Contractor.

The following shall be marked in all instances:-

(a)
Fuse. The rating and circuit identification of each fuse shall be marked adjacent to the fuse base.

(b)
Control and Indicating Devices. The function of each control and indication device shall be marked. The caption and its arrangement shall be subject to the approval of the Engineer.

(c)
Pre-set Controls. The circuits reference and if possible, the function, shall be marked adjacent to each pre-set control in a position where it will be clearly visible while the adjustment is being made.

(d)
Connectors. The diagram reference number shall be marked on, or adjacent to each connector.

(e)
Test Points shall be individually marked with the diagram reference number.

All junction boxes shall include a record pasted inside the lid showing the terminal allocation.

Each terminal of a screw type terminal block shall bear the identification marking either on the body of the block, or adjacent to it. All other terminal blocks shall be marked with their circuit designations and rows shall be marked to identify each connection to the approval of the Engineer.

All wiring shall be identifiable by an approved colour code, ferrules marked with the nomenclature adopted for these conductors, on the manufacturer's diagrams, or by circuit reference at the terminals.

3.7
Bolts and nuts

All bolts, studs, screw threads, pipe thread, bolt heads and nuts shall be of ISO metric standard type.  

Except for small wiring, current carrying terminal bolts or studs, for mechanical, shall not be less than 6 mm in diameter.

All nuts and pins shall be adequately locked.

Wherever possible bolts shall be fitted in such a manner that in the event of failure of locking resulting in the nuts working loose and falling off, the bolt will remain in position.

All bolts, nuts and washers placed in outdoor positions shall be treated to prevent corrosion of the threads and electrolytic action between dissimilar metals.

Where bolts are used on external horizontal surfaces where water can collect, methods of preventing the ingress of moisture to the threads shall be provided.

Each bolt or stud shall project at least one thread but not more than four threads through its nut, except when otherwise approved for terminal board studs or relay stems.  If bolts and nuts are placed so that they are inaccessible by means of ordinary spanners, special spanners shall be provided.

The length of the screwed portion of the bolts shall be such that no screw thread may form part of a shear plane between members.

Taper washers shall be provided where necessary.

3.8
Cleaning and painting

Before painting or filling with oil, gas or compound, all ungalvanized parts shall be thoroughly cleaned, free from rust, scale, burrs, grease and moisture and all external rough surfaces on casting shall be filled.  

The following minimum painting requirements shall apply to all ferrous parts unless the supplier can show, to the satisfaction of the Engineer, that any alternative he proposes is in all respects equal or superior to the specified requirements:  

3.8.1
External surfaces at works

	Apparatus
	Painting

	All ungalvanized surfaces, other than nuts, bolts and washers, which may be removed for maintenance purposes, for use outdoors
	i.
One priming coat of corrosion inhibiting paint applied immediately after cleaning  

ii.
Two coats of non-glossy, oil- and weather-resisting paint applied after inspection and testing and before despatch

iii.
One finishing coat of glossy oil and water resisting non-fading paint before despatch. 

	Exposed, ungalvanized nuts, bolts and washers which may be removed for maintenance purposes, for use outdoors
	One coat of oil - and weather-resisting, non-fading paint applied.  

	Panels, cubicles, kiosks and apparatus boxes, for use indoors
	Three coats of paint, the colour and finish of the final coat to be to the approval of the Engineer.  

Grey colour is preferable.  


3.8.2
Internal surfaces

	Apparatus
	Painting

	Oil filled chambers and tanks
	One coat of oil resisting varnish or paint

	Kiosks and apparatus boxes for use outdoors
	Three coats of paint, the final coat being an anti-condensation finish coloured white or light grey  

	Cubicles, kiosks and apparatus boxes for use indoors
	Three coats of paint, the final coat being a white or light colour.  


Successive coats of paint shall be easily distinguishable by shade of colour and shall be applied to a clean, dry and properly prepared surface.  Each coat shall be compatible with the previous coat.  

All paintwork which has been damaged during transport or erection shall be made good to the approval of the Engineer.  

The colour and shade of all painted external surfaces shall be to the approval of the Engineer.  

3.9
Insulating oil and gas

Unless otherwise specified, sufficient oil or gas shall be supplied to fill all equipment provided under this Contract.  The oil or gas shall be of appropriate type and suitable in all respects for use in the equipment when it is operated under the conditions laid down in this Specification.  The insulating medium used shall comply with the relevant IEC Specification.  

3.10
Prevention of acidity

The design, and all materials and process used in construction of the equipment, shall be such as to reduce to a minimum the risk of development of acidity in the oil or gas.  

3.11
Fire precautions

All apparatus, connections and cabling shall be designed and arranged to minimize the risk of fire and any damage which might be caused in the event of fire.  

3.12
Corona and radio interference

All equipment shall be designed so as to minimize corona or other electrical discharge and radio interference.  

3.13
Locking devices and padlocks

All padlocks, locks and keys required to secure switchgear and other equipment shall be supplied on this Contract.  

Access doors to equipment including circuit breakers, isolating devices, screened enclosures, cubicles and marshalling kiosks and all equipment operating handles, local control and selector switches, valves, switchgear shutters and maintenance positions shall be lockable.  

All padlocks and other locks shall be provided with two identical keys and both the key and the lock shall be impressed with the manufacturer’s serial number.  Except where a master key is specially requested or it has been otherwise agreed, it shall be impossible to open any padlock or lock with the key of any other padlock or lock provided on this Contract.  

When requested, wall mounting lockable cabinets with glazed doors, suitable for accommodation of padlocks and keys whilst not in use, shall be provided.  They shall be mounted in approved positions and shall be labelled in a similar manner to the keys.  The engraving on all labels shall be in accordance with a scheme to be agreed with the Engineer.  

3.14
Tools

The Supplier shall provide any special tools that may be required for making adjustments to equipment during normal operation and maintenance.  These tools are to be of alloy steel and shall be contained in steel boxes, complete with locks and keys.  

All tools shall be stamped in an approved manner for identification purposes.  

3.15
Erection marks

All plant that requires assembly at Site shall have distinguishing marks on it to facilitate erection and to identify the material in relation to drawings, material lists or shipping documents.  All marks shall be legible and easily visible.  Where relevant, erection marks shall be stamped before galvanizing and shall be clearly visible after galvanizing.  

3.16
Operating and maintenance instructions

Operating and maintenance instructions form part of this Contract and shall be provided in accordance with the Conditions of Contract.  

3.17
Spare parts

Particulars of spare parts, which may or may not form part of the Contract at the Engineer’s discretion, shall be given in Schedule J.  

3.18
Manufacturing experience and qualifications

To be considered as a possible Supplier of XLPE insulated cable the Tenderer shall submit with his Tender in addition to the other official information specified in Volume 1 of the Tender Document information to prove that the proposed cable manufacturer can comply with the following requirements:

a) Ten years continuous experience in the manufacture of the type and size specified herein, signed, stamped and witnessed.

b) The manufacturer's works include a testing facility capable of carrying out all specified tests including type tests.

c) The procurement of materials and cable manufacture are governed by acceptable quality assurance procedures in accordance with a Quality Assurance Manual to be submitted with the Tender.

d) The XLPE extrusions shall be chemically cross-linked and the cable shall be vulcanised by a dry curing process. 

e) Actual type test certificates, signed, stamped and witnessed, to show that the type and size of cable specified herein meets the partial discharge requirements in Section 5 hereafter.

3.19
Quality Assurance system

The supplier must hold ISO 9002 (alternatively ISO 9001) certification of their quality assurance procedures.  Evidence of such certification must be submitted with the Tender.  

Where an equivalent certification to ISO 9002 (alternative ISO 9001) is offered, details of the system, the certification body and the frequency and type of audits, both internal and external, shall be submitted with the Tender.  The equivalent certification shall be subject to review, evaluation and approval by JEPCO or its appointed representative(s).  

4
11& 33 KV WTR-XLPE INSULATED CABLES
4.1
GENERAL REQUIREMENTS
All XLPE cables shall comply with the current editions of IEC 60502, VDE0273, ICEA/NEMA: S-66-524 / WC 7-1982 and other equivalent and related National Standards, subject to the variations and additions stated herein.

All cables shall be suitable for operation under the respective loads and such sudden variations of load and voltage as may be met with under working conditions on the system, and in the climatic conditions prevailing on site. See Section 2: Site and Design Particulars.
4.2
Rated Voltage

The rated voltage of the cables in this tender are Uo/U(Um) = 8.7/15(17.5) kV for items 1, 2 and 3, and Uo/U(Um) = 19/33(36) kV for items 4, 5 and 6 where Uo, U and Um as defined in IEC 60502.
4.3
CONDUCTOR
The conductors shall be circular, stranded and compacted hard drawn aluminium for all items. With cross section detailed in schedule 'G1'. The conductor shall be in accordance with the requirements of IEC 60228 or an equivalent national standard.
The maximum continuous current carrying capacity, the maximum permissible continuous conductor temperature, and the factors for determining such rating and temperature shall be based on IEC Standard 61187 or other approved Standards and subsequent amendments.
4.4
INSULATION AND SCREENING

4.4.1
CONDUCTOR SCREEN
Conductor screening shall consist of a layer of thermosetting extruded semi-conducting compound of adequate thickness having a smooth even surface in intimate contact with the cable insulation and the conductor, but easily strippable from the conductor surface. The minimum thickness at any point shall not fall below 0.3 mm.
4.4.2
WTR-XLPE INSULATION 

The insulation shall be dry-cured water tree retardant (WTR) cross-linked polyethylene (XLPE) with a nominal thickness of 4.5mm (minimum average) for 15 KV and 8mm (minimum average) for 33 KV with difference between the largest and the smallest value of the insulation thickness measured in one level shall not  exceed 0.6mm and 0.9mm respectively. XLPE insulated cables shall be designed for a maximum continuous conductor temperature of 90 degrees C, and a maximum short-circuit temperature of 250 degrees C, XLPE Insulation material and thickness shall meet all the relevant requirements of IEC 60502 and IEC 60811 or other approved standards. 
XLPE insulation material shall be from only either Borealis Company (TYPE SuperTR LE4212) or Dow Chemicals Company (Type HFDC-4202).
4.4.3
INSULATION SCREEN
Insulation screening shall consist of a layer of thermosetting extruded semi-conducting compound firmly bonded to the insulation, having a smooth even surface in intimate contact with the cable insulation. The thickness of this layer shall range between 0.3 and 0.6mm. The difference between the largest and smallest value of the diameter over the extruded insulation screening, measured in one level, shall not exceed 0.5mm.  
4.4.4
METALLIC SCREEN
The metallic portion of the screen shall be plain annealed copper with a wire design together with a copper contact tape applied helically, and shall be of adequate cross-sectional area to carry the prospective earth fault current of the system. Gaps in the screen shall comply with national regulations and/or standards.

The nominal cross section of the copper wire shall not be less than 70mm2 for items 2, 3, 4 and 5, and 16 mm2 for items 1 and 6.

4.4.5
LONGTUDINAL WATERTIGHTNESS LAYERS

The screen area shall be watertight in the longitudinal direction by means of two layers of semi conductive swellable tapes with one layer under and the second layer over the metallic screen. 

4.4.6
OUTER SHEATH
The outer sheath shall consist of extruded black high density polyethylene type ST7 to IEC 60840 with a Shore hardness (D) of not less than 55. It shall be coated with graphite powder as a conducting material, to act as an electrode for work and site voltage tests to verify the integrity of the sheath.     

The nominal thickness of the sheath shall be in accordance with IEC 60502 or other approved Standards. The smallest nominal value shall not be less than 2.5 mm. The minimum thickness at any point shall not fall below 85% of the nominal value by more than 0.1mm.
The extruded over sheaths of cables shall be engraved with white P.E. powder or other approved means with the following:- cable voltage designation, the conductor size, and the words "ELECTRIC CABLE” in English, Tender number, manufacturer’s name, year of manufacture and JEPCO’s name. The length in meters shall be also engraved on the outer sheath all along each cable length at each meter. The letters and figures shall consist of upright block characters arranged along two or more lines approximately equally spaced around the circumference of the cable. The maximum height of the characters shall be 13 mm and the minimum size 15 per cent of the approximate overall diameter of the cable or 3 mm whichever is the greater. The space between the end of one set of engraved characters and the beginning of the next shall not be greater than 150 mm.
4.5
SEALING AND DRUMMING

The cable shall be wound onto strong steel or wooden returnable drums arranged to take a round spindle of a section adequate to support the loaded cable drum during installation and handling. The drum shall be lagged with strong closely fitted battens which shall be constructed of seasoned timber to prevent shrinkage of drums during shipment and subsequent storage on site. Each drum shall be clearly marked in a manner which cannot be obliterated with the particulars of the cable including voltage, length, conductor size, number of cores, type of protective covering, section number, gross and net weight, together with the direction for rolling. Caps to prevent the ingress of moisture and the end of the cable left projecting from the drum shall at all times be securely protected against damage by mis-handling during transport and storage. Drum capacity shall be 1000 m for 1-core cables.
5.
MULTIPAIR THERMOPLASTIC INSULATED CABLES

5.1
General

These cables are required for light current control functions or for installation alongside power cables over long routes to provide feeder pilot protection, speech and data transmission circuits. The former cables will be insulated with PVC and the latter with polyethylene insulation. A means of identifying the manufacturer shall be incorporated throughout the length of each cable.

5.2
Conductors

The conductors shall be copper and they shall comply with B.S.6360 or equivalent. Where tinned conductors are specified their solder-ability performance shall conform to the test requirements of B.S.2011 or equivalent. The size of conductors shall be 1/0.9 mm and the number of pairs shall be as stated in Schedules 'A' and 'D'.

5.3
Thermoplastic Insulation

The PVC insulation shall be type 2 compound as defined in B.S.6746 or equivalent. The polyethylene insulation shall be type 03 compound in accordance with B.S.6234 or equivalent. The thickness of insulation shall be as stated in Schedule 'D' and shall be verified in the manner prescribed in Clause 18 of B.S. 6346, or equivalent.

5.4
Core Identification

The cores shall be identified by colours with distinctive schemes to discriminate between PVC and polyethylene insulation. The colour schemes shall be approved by the Engineer when not specified in detail and shall be the generally accepted schemes and rotation for the appropriate design of cable.

5.5
Twinning and Laying-Up

The insulated cores shall be twisted together to form a pair. In the case of PVC insulated conductors the required number of pairs shall be laid up to form a compact symmetrical cable with the two pair construction laid up in quad formation.

Regarding the pairs of polythylene insulated conductors the length of lay shall differ between adjacent pairs and the lay shall be so selected as to minimise crosstalk. The arrangement of pairs shall be in accordance with the conventional construction for this type of cable. In the case of seven pair cables six pairs shall be laid around a centre pair and in each succeeding layer the number of pairs shall be increased by six pairs over the number in the preceding layer to provide a uniform structure. No fillers shall be used in these cables.

Binding tapes constructed from suitable materials shall be applied with open spiral or overlap as required between layers, where necessary, and over the laid up structure to provide a compact uniform formation. A rip cord to facilitate removal of the inner sheath of PVC insulated cables may be included during the application of the overall binding tape.

5.6
Inner Sheath

The extruded inner bedding sheath shall be black and for PVC insulated cables shall consist of PVC compound type 1 or 6 in accordance with B.S. 6746 or equivalent. The black polyethylene compound for the inner sheaths of polyethylene insulated cables shall be type 03C in accordance with B.S.6234 or equivalent. The thickness of inner sheath shall be verified in the manner prescribed in Clause 19 of B.S.6346 or equivalent.

5.7
Wire Armour

The cables shall be armoured with one layer of galvanised steel wires conforming to the requirements of B.S.1442 or equivalent. The number and diameter of the wires shall be as stated in Schedule 'D'. Where pilot cables are likely to be subjected to induced voltages in excess of 15 kV the cables shall be armoured with aluminium wire in accordance with the requirements of B.S.2627 or equivalent, condition H.68, to limit the induced voltage. The armour shall be coated with a waterproof protecting compound.

5.8
Oversheaths

While bright wire armoured cables may be specified for installation indoors in air, free from corrosive elements, the cables for all other situations shall be provided with an extruded oversheath of black PVC compound conforming to Type 1 in B.S.6746 or equivalent. A coating  of graphite powder as a conducting material shall be applied over the extruded covering to act as an electrode for the works and site voltage tests to verify the integrity of the oversheath.

The oversheath shall be embossed in conformity with the requirements of Clause 14.2 of B.S.6346 or equivalent with the following legends:-

PVC Multipair Cables

- 'ELECTRIC CABLE - 100 V'

Polyethylene Multipair Cables
- 'ELECTRIC CABLE - TELE'

5.9
Sealing and Drumming

The sealing and drumming of these cables shall be in accordance with the requirements for Power Cables and Accessories. In addition the rotation or colour sequence of the cores at the running end which shall be marked 'Red' shall be agreed with the Engineer and shall be the same for all drum lengths unless otherwise stated. The inner end of these cables shall be marked 'Green'.

5.10
Testing

The tests stipulated in this Specification shall be carried out on all cables to verify that they conform to the specified requirements
The extruded oversheath of all cables included in this Specification shall also have the following information engraved on it:

· JEPCO. NAME 

· CONTRACT NO.

· CABLE SIZE + VOLTAGE.

· DATE OF MANUFACTURING.

· Manufacturer Name.

· The length in meter for each meter all along each cable.

6
WORKS TESTS FOR CABLES 

6.1
General Requirements

All cables, accessories and equipment shall be subjected to and withstand satisfactorily   the test requirements detailed in this specification. All materials shall withstand  such routine tests as are customary in the manufacture of cables and accessories included  in the Contract.

Not less than fourteen days' notice in writing shall be given to the Engineers in order that they may arrange to be present if they so desire. The Supplier shall arrange to conduct as many tests together as are possible in the opinion of the Engineer and shall submit six copies of the records of such to the Engineer within seven days of completion.

All instruments used in the testing shall be approved by the Engineer. If any doubt arises concerning the accuracy of any instrument the Supplier shall, if required by the Engineer, have the instrument calibrated at his own expense by the appropriate Standards Laboratory or such other body as may be approved.

Test voltages shall be measured by means of either an electro-static voltmeter or crest voltmeter connected to the higher voltage side of the transformer supplying the test voltage or by a suitable instrument connected to the lower voltage side, calibrated by means of a sphere spark gap in accordance with B.S. 358 or equivalent. In all electrical tests, if the r.m.s. voltage is not measured directly it shall be calculated in an approved manner. The frequency of the testing supply shall be in the range 40 Hz to 62 Hz.
6.2
Galvanising
Samples of all galvanised material selected by the Engineer shall be subjected to the galvanising test requirements set out under B.S. 443, B.S.729 or equivalent, whichever is applicable to the type of material under test.
6.3
XLPE Insulated Power Cables

6.3.1
Type Tests (Electrical and Non-electrical)

The Supplier shall carry out the type tests detailed in the current issue  of  IEC 60502 /  BS 6622/ VDE 0273/  ICEA/NEMA:S-66-524/WC 7-1982.

These type tests requirements may be waived on production of documentary proof that samples of similar cable manufactured in the same works with the equivalent or larger conductor section have passed identical or more onerous tests which have been witnessed by an approved electricity authority or their duly appointed representatives. Failure by the Contractor to provide such documentary proof in advance of cable manufacture commencing will render the Contractor liable to carry out the full type test programme in entirety.

However, the partial discharge test for items 1, 2 and 3  shall be conducted at 2 Uo = 2x8.7 = 17.4 kV AC with a maximum acceptable discharge not exceeding 2 pC. And the partial discharge test for item 4 shall be conducted at 2 Uo = 2x19 = 38 kV AC with a maximum acceptable discharge not exceeding 2 pC.
The test procedure shall be performed by qualified and well-recognized testing laboratories such as CBLT accredited laboratories.

6.3.2
Routine Tests

Routine tests shall be carried out on completed cable lengths of XLPE insulated power cable as detailed in, and in accordance with, the current issues of IEC 60502 and BS 6622 or other approved Standards, and shall be ready to withstand any of the tests detailed in VDE 0273/12.87 should the Engineer see that fit, and shall include the following:

a) Measurements of electrical resistance of conductors.
b) High voltage test.

c) Partial discharge test: where detectable discharge shall not exceed 2 pC at 2 Uo . 
6.3.3
Ageing Test

The manufacturer shall perform ageing tests in accordance with IEC-60811-1-2 and IEC-60811-2-1. The supplier shall provide the necessary documentations associated with the performance of ageing test for power cables. 
6.3.4
Special Tests

The Supplier shall carry out the special tests detailed in the current issue of IEC 60502 or other approved standards and shall include the following:

a) Conductor examination.

b) Check of dimensions.

c) Electrical and voltage tests for cables.

d) Hot set test for XLPE insulation.

e) Breaking load and elongation for XLPE insulation and PVC sheaths.

f) Galvanised wires tensile strength and thickness of galvanised coating.

g) Longitudinal watertightness test.

6.4
Polyethylene Insulated Multipair Cables

6.4.1
Routine Tests on Completed Cable

a) Conductor Resistance - The d.c. resistance of the conductors shall be measured and the results, when corrected in accordance with Table 9 of B.S.6360 or equivalent shall not exceed 58.2 ohms for 1,000 m loop at 20 deg. C.

b) Voltage Test - The voltage test shall be made with alternating current of approximately sine wave form at any frequency from 40-62 Hz inclusive. The voltage shall be increased gradually to the r.m.s. values specified below and maintained continuously for one minute between conductors or between all conductors and the armour which shall be earthed. No breakdown of the insulation shall occur.
	Cables designed to withstand induced voltage not exceeding 15 kV
	10 kV a.c. between conductors*
15 kV a.c. between conductors and armour*


* Where limitations in the capacity of the testing equipment preclude an a.c. test an alternative d.c. test voltage of twice the a.c. test voltage applied for one minute is acceptable.

c) Mutual Capacitance - The mutual capacitance shall be measured between the conductors comprising each pair with all other conductors and any screen connected to the armour and the earth. The mean value obtained using alternating current and a suitable bridge instrument shall be recorded.

[image: image1.jpg]


d) Capacitance Unbalance - Measurements of pair to pair capacitance unbalance shall be made at a suitable audio frequency with all other conductors and any screen connected to the armour and earthed. The measured values shall be divided by:-

Where L is the length in meters. Lengths less than 100 meters shall be considered as 100 meters. The corrected unbalanced measurements shall not exceed 50 pF for carrier  pairs and for other pairs 500 pF. Measurements will normally be made between adjacent pairs, to limit the amount of testing, except in the case of carrier pairs where all combinations shall be measured.

[image: image2.wmf]ú

û

ù

+

ê

ë

é

500

500

2

1

L

L

e) Mutual inductance - Where cables are specified with nominated carrier pairs the mutual inductance shall be measured at 5 kHz. The measured values shall be divided by:-

Where L is the length in meters. Lengths less than 100 metres shall be considered as 100 meters. The mutual inductance shall not exceed 0.50 mH after correction.

f) Insulation Resistance - The insulation resistance shall be measured between each conductor and the other conductors and any screen connected to the armour after the application of 500 V d.c. for one minute. The measured values shall not be less than the value at 20 deg. C specified in Schedule 'D'.

g) Electrical Tests on Extruded PVC Oversheath coated with graphite powder - The oversheath shall withstand a d.c. voltage test equal to 8 kV per mm of sheath thickness applied between the armour and the outer conducting coating for one minute.

The Contractor may submit, for the Engineer's approval proposals for limited or facilitating the testing procedure on multicore cables. Approval will be subject to the test result being acceptable otherwise the tests will have to be repeated on individual pairs.

6.4.2
Sample Tests

A representative number of tests shall be carried out on samples of thermoplastic insulation and sheath in the manner prescribed in B.S. 6746 and B.S. 6234 or equivalent. The compounds shall conform to the requirements and values stated therein.

6.4.3
Galvanising

Samples of all galvanised material selected by the Engineer shall be subjected to the galvanising test requirements set out under B.S.443, B.S.729 or equivalent, whichever is applicable to the type of material under test.
Schedule A2 

Summary Schedule

Technical and Commercial Data

Note: The following schedule represents the most essential data based on which the evaluation process shall be performed.
	item
	Description
	Quantity
	unit CPT JEPCO Stores

 Price/ Currency
	Total CPT JEPCO Stores

 Price/ Currency
	Variation in price per 1000 meters
	Delivery

(Weeks)

	1.
	8.7/15 kV, 120 mm2 Al., 1-CORE, WTR-XLPE CABLE
	10
	
	
	Al:-
Cu:-
	

	2.
	8.7/15 kV, 240 mm2 Al., 1-CORE, WTR-XLPE CABLE
	50
	
	
	Al:-
Cu:-
	

	3.
	8.7/15 kV, 400 mm2 Al., 1-CORE, WTR-XLPE CABLE
	600
	
	
	Al:-
Cu:-
	

	4.
	19/33 kV, 300 mm2 Al., 1-CORE, WTR-XLPE CABLE
	60
	
	
	Al:-
Cu:-
	

	5.
	19/33 kV, 500 mm2 Al., 1-CORE, WTR-XLPE CABLE
	300
	
	
	Al:-
Cu:-
	

	6.
	19/33 kV, 70 mm2 Al., 1-CORE, WTR-XLPE CABLE
	Not Required
	
	
	Al:-
Cu:-
	

	Basic Prices for Aluminum U.S. Dollar per Ton: 3,000 $                                  
Basic Prices for Copper U.S. Dollar per Ton: 13,000 $


SCHEDULE B
TIME PERIODS FOR PROCUREMENT, DESIGN, MANUFACTURE,
INSPECTION, TESTING, completion AND DELIVERY

(To be completed by the Tenderer)

Note 1

All time periods are weeks from date of Contract Placement.

Note 2

For purposes of Tender Evaluation, the time from commencement date within which the material is required to be delivered to CPT JEPCO Stores-Zarqa shall be less than 16 weeks.

	Description
	Item 1 - 5

weeks

	Time within which all arrangement and equipment drawings shall be submitted for approval.

Time within which all material shall be available for final inspection and testing in works.

Time within which the plant shall be packed and delivered to the Docks (FOB).

Time within which the plant shall be packed and delivered to JEPCO Stores.
	
………



………



………

………


SCHEDULE C
MANUFACTURERS AND PLACES OF MANUFACTURE,
TESTING AND INSPECTION

(To be completed by the Tenderer)

	Item 1, 2, 3, 4, 5, 6: XLPE INSULATED CABLE
	Manufacturer
	Place of Manufacture
	Place of Testing & Inspection*

	1.
	Complete cable.
	……………..
	……………..
	…………….

	2.
	Outersheath Material
	……………..
	……………..
	…………….

	3.
	Watertight Tape
	……………..
	……………..
	…………….

	4.
	Copper
	……………..
	……………..
	…………….

	5.
	WTR-XLPE Material
	……………..
	……………..
	…………….

	6.
	Aluminium
	……………..
	……………..
	…………….


	SCHEDULE D
TECHNICAL DATA,
8.7/15kV, 1-core XLPE INSULATED CABLES

(To be completed by the Tenderer)

	Item
	Data Required
	
	Item 1.
120 mm2,
 Al CABLE
	Item 2.
240 mm2,
 Al CABLE
	Item 3.
400 mm2, 
Al CABLE

	1
	Conductor
	
	
	
	

	1.1
	Shape of conductor
	
	-------------
	-------------
	-------------

	1.2
	Number of conductor
	
	-------------
	-------------
	-------------

	1.3
	Sectional area of conductor
	mm2
	-------------
	-------------
	-------------

	1.4
	Diameter of conductor
	mm
	-------------
	-------------
	-------------

	1.5
	Number and diameter of wires in each conductor
	
No./mm
	-------------
	-------------
	-------------

	2
	Extruded conductor screen
	
	-------------
	-------------
	-------------

	2.1
	Material
	
	-------------
	-------------
	-------------

	2.2
	Nominal thickness
	mm
	-------------
	-------------
	-------------

	2.3
	Minimum thickness
	mm
	-------------
	-------------
	-------------

	3
	WTR-XLPE Insulation
	
	
	
	

	3.1
	Nominal thickness
	mm
	-------------
	-------------
	-------------

	3.2
	Minimum thickness at any point
	mm
	
-------------
	
-------------
	
-------------

	3.3
	Details of vulcanization process
	
	
-------------
	
-------------
	
-------------

	4
	Insulation Screen
	
	-------------
	-------------
	-------------

	4.1
	Material
	
	-------------
	-------------
	-------------

	4.2
	Nominal thickness
	mm
	-------------
	-------------
	-------------

	4.3
	Minimum thickness
	mm
	-------------
	-------------
	-------------

	4.4
	Type (easily strippable or firmly bonded )
	
	-------------
	-------------
	-------------

	5.
	Copper screen
	
	-------------
	-------------
	-------------

	5.1
	Cross-sectional area
	mm2
	-------------
	-------------
	-------------

	5.2
	No. of copper wires
	
	-------------
	-------------
	-------------

	5.3
	Nominal diameter of wire
	mm
	-------------
	-------------
	-------------

	5.4
	Copper tape thickness / width
	
	
-------------
	
-------------
	
-------------

	6.
	Watertightness Layers
	
	-------------
	-------------
	-------------

	6.1
	No. of Swelling tapes layers.
	
	-------------
	-------------
	-------------

	6.2
	Thickness of each layer
	mm
	-------------
	-------------
	-------------

	6.3
	Thickness of outer extruded semiconductive layer over each core.
	
	-------------
	-------------
	-------------

	7
	Nominal diameter over extruded semiconducting layer mentioned in 6.3
	

mm
	

-------------
	

-------------
	

-------------

	8
	Nominal diameter over metallic screen
	
mm
	-------------
	-------------
	-------------

	9
	Outer Extruded Sheath
	
	-------------
	-------------
	-------------

	9.1
	Material
	
	-------------
	-------------
	-------------

	9.2
	Nominal thickness
	mm
	-------------
	-------------
	-------------

	10
	Nominal external diameter of completed cable
	
mm
	
-------------
	
-------------
	
-------------

	11
	Nominal weight per meter of completed cable 
	
kg
	
-------------
	
-------------
	
-------------

	12
	Minimum radius of bend around which cable can be laid
	

m
	

-------------
	

-------------
	

-------------

	13
	Nominal internal diameter of pipes or ducts
	
mm
	
-------------
	
-------------
	
-------------

	14
	Manufacturing drum lengths
	
	-------------
	-------------
	-------------

	14.1
	Normal
	m
	-------------
	-------------
	-------------

	14.2
	Maximum
	m
	-------------
	-------------
	-------------

	15
	Maximum d.c. resistance of conductor per 1,000m of cable at 20oC
	

ohm
	

-------------
	

-------------
	

-------------

	16
	Maximum a.c. resistance of conductor per 1,000m of cable at 20oC
	

ohm
	

-------------
	

-------------
	

-------------

	17
	Equivalent star reactance per 1,000m of cable at 50Hz
	
ohm
	
-------------
	
-------------
	
-------------

	18
	Maximum equipment star capacitance per 1,000m of cable 
	

µF
	

-------------
	

-------------
	

-------------

	19
	Maximum charging current per conductor per 1,000m of cable at normal voltage and frequency
	


A
	


-------------
	


-------------
	


-------------

	20
	Maximum continuous current carrying capacity per conductor when laid direct in the ground at depth of 1000mm. Assume g = 1.2 deg.C. m/W and ground temperature 300C.
	





A
	





-------------
	





-------------
	





-------------

	20.1
	One three-phase circuit per trench.
	
A
	
-------------
	
-------------
	
-------------

	20.2
	Two three-phase circuit 450mm spaced per trench.
	
A
	
-------------
	
-------------
	
-------------

	21
	Maximum continuous current carrying capacity per conductor when drawn into pipes or ducts at a depth of 1000mm. Assume g = 1.2 deg.C. m/W and ground temperature 300C.
	





A
	





-------------
	





-------------
	





-------------

	21.1
	One three-phase circuit.
	A
	-------------
	-------------
	-------------

	21.2
	Two three-phase circuit 450mm spaced.
	A
	-------------
	-------------
	-------------

	22
	Maximum continuous current carrying capacity per conductor when installed in air at an ambient temperature 40o.C One 3-phase circuit
	




A
	




-------------
	




-------------
	




-------------

	23
	Screen loss per 1,000 m of 3 phase circuit at normal working voltage and frequency and at maximum current ratings given in Item 20.1
	




kW
	




-------------
	




-------------
	




-------------

	24
	Minimum insulation resistance at 20o C per 1,000 m of one conductor to Screen, the remaining conductors being connected to the Screen 
	




Mohm
	




-------------
	




-------------
	




-------------

	25
	Earth fault short circuit current carrying capacity when cable is loaded as in item 20.1 before S/C and conductor temperature 90oC
	



kA
	



-------------
	



-------------
	



-------------

	25.1
	Rating of copper screen per core:-

a) 1 sec.

b) 3 sec.

c) Final screen temperature
	kA

kA

oC
	-------------

-------------

-------------
	-------------

-------------

-------------
	-------------

-------------

-------------

	26
	Conductor short circuit current permissible when S/C occurs at conductor temp. of 90oC. for a period of:-

0.2 Seconds

0.4 Seconds

0.6 Seconds

0.8 Seconds

1.0 Seconds

2.0 Seconds

3.0 Seconds

Final conductor temperature
	kA

kA

kA

kA

kA

kA

kA

oC
	-------------

-------------

-------------

-------------

-------------

-------------

-------------

-------------
	-------------

-------------

-------------

-------------

-------------

-------------

-------------

-------------
	-------------

-------------

-------------

-------------

-------------

-------------

-------------

-------------

	27
	Maximum dielectric stress at nominal voltage:-
	
	-------------
	-------------
	-------------

	27.1
	At conductor screen
(assumed smooth)
	
MV/m
	
-------------
	
-------------
	
-------------

	27.2
	At core screen
	MV/m
	-------------
	-------------
	-------------

	28
	Impulse withstand voltage:-

(a) positive 1.2/50 wave 

(b) negative 1.2/50 wave
	kVP

kVP
	-------------

-------------
	-------------

-------------
	-------------

-------------

	29
	Partial discharge voltage
Guaranteed maximum discharge
	kV


pC
	-------------


-------------
	-------------


-------------
	-------------


-------------

	30
	Tan ( measurment as a function of voltage:-
At 0.5 Uo.

At Uo.

At 2.0 Uo.

Max. difference between 0.5Uo and 2.0Uo.
	
	-------------

-------------

-------------


-------------
	-------------

-------------

-------------


-------------
	-------------

-------------

-------------


-------------

	31
	Tan ( measurement as a function of temperature:-
At ambient temperature.

At max. operating temperature (90oC).
	
	-------------


-------------
	-------------


-------------
	-------------


-------------

	32
	How the information will appear on the outer sheath.
	
	
-------------
	
-------------
	
-------------

	33
	Is the length in meter along the cable appear at each meter.
	

Y/N
	

-------------
	

-------------
	

-------------

	34
	Number of years experience in the production of the type and size of cables specified herein
	
	


-------------
	


-------------
	


-------------

	35
	Has ageing test been performed in accordance with the applicable IEC standards
	


Y/N
	


-------------
	


-------------
	


-------------

	36
	Name and location of testing laboratories.
	
	
-------------
	
-------------
	
-------------


	SCHEDULE D
TECHNICAL DATA,
19/33kV, 1-core XLPE INSULATED CABLES

(To be completed by the Tenderer)

	Item
	Data Required
	
	Item 4
300 mm2, Al CABLE
	Item 5
500 mm2, Al CABLE
	Item 6
70 mm2, Al CABLE
(Not Required)

	1
	Conductor
	
	-------------
	-------------
	-------------

	1.1
	Shape of conductor
	
	-------------
	-------------
	-------------

	1.2
	Number of conductor
	
	-------------
	-------------
	-------------

	1.3
	Sectional area of conductor
	mm2
	-------------
	-------------
	-------------

	1.4
	Diameter of conductor
	mm
	-------------
	-------------
	-------------

	1.5
	Number and diameter of wires in each conductor
	
No./mm
	-------------
	-------------
	-------------

	2
	Extruded conductor screen
	
	-------------
	-------------
	-------------

	2.1
	Material
	
	-------------
	-------------
	-------------

	2.2
	Nominal thickness
	mm
	-------------
	-------------
	-------------

	2.3
	Minimum thickness
	mm
	-------------
	-------------
	-------------

	3
	WTR-XLPE Insulation
	
	-------------
	-------------
	-------------

	3.1
	Nominal thickness
	mm
	-------------
	-------------
	-------------

	3.2
	Minimum thickness at any point
	mm
	
-------------
	
-------------
	-------------

	3.3
	Details of vulcanization process
	
	
-------------
	
-------------
	-------------

	4
	Insulation Screen
	
	-------------
	-------------
	-------------

	4.1
	Material
	
	-------------
	-------------
	-------------

	4.2
	Nominal thickness
	mm
	-------------
	-------------
	-------------

	4.3
	Minimum thickness
	mm
	-------------
	-------------
	-------------

	4.4
	Type (easily strippable or firmly bonded )
	
	-------------
	-------------
	-------------

	5.
	Copper screen
	
	-------------
	-------------
	-------------

	5.1
	Cross-sectional area
	mm2
	-------------
	-------------
	-------------

	5.2
	No. of copper wires
	
	-------------
	-------------
	-------------

	5.3
	Nominal diameter of wire
	mm
	-------------
	-------------
	-------------

	5.4
	Copper tape thickness / width
	
	
-------------
	
-------------
	-------------

	6.
	Watertightness Layers
	
	-------------
	-------------
	-------------

	6.1
	No. of Swelling tapes layers.
	
	-------------
	-------------
	-------------

	6.2
	Thickness of each layer
	mm
	-------------
	-------------
	-------------

	6.3
	Thickness of outer extruded semiconductive layer over each core.
	
	-------------
	-------------
	-------------

	7
	Nominal diameter over extruded semiconducting layer mentioned in 6.3
	

mm
	

-------------
	

-------------
	-------------

	8
	Nominal diameter over metallic screen
	
mm
	-------------
	-------------
	-------------

	9
	Outer Extruded Sheath
	
	-------------
	-------------
	-------------

	9.1
	Material
	
	-------------
	-------------
	-------------

	9.2
	Nominal thickness
	mm
	-------------
	-------------
	-------------

	10
	Nominal external diameter of completed cable
	
mm
	
-------------
	
-------------
	-------------

	11
	Nominal weight per meter of completed cable 
	
kg
	
-------------
	
-------------
	-------------

	12
	Minimum radius of bend around which cable can be laid
	

m
	

-------------
	

-------------
	-------------

	13
	Nominal internal diameter of pipes or ducts
	
mm
	
-------------
	
-------------
	-------------

	14
	Manufacturing drum lengths
	
	-------------
	-------------
	-------------

	14.1
	Normal
	m
	-------------
	-------------
	-------------

	14.2
	Maximum
	m
	-------------
	-------------
	-------------

	15
	Maximum d.c. resistance of conductor per 1,000m of cable at 20oC
	

ohm
	

-------------
	

-------------
	-------------

	16
	Maximum a.c. resistance of conductor per 1,000m of cable at 20oC
	

ohm
	

-------------
	

-------------
	-------------

	17
	Equivalent star reactance per 1,000m of cable at 50Hz
	
ohm
	
-------------
	
-------------
	-------------

	18
	Maximum equipment star capacitance per 1,000m of cable 
	

µF
	

-------------
	

-------------
	-------------

	19
	Maximum charging current per conductor per 1,000m of cable at normal voltage and frequency
	


A
	


-------------
	


-------------
	-------------

	20
	Maximum continuous current carrying capacity per conductor when laid direct in the ground at depth of 1000mm. Assume g = 1.2 deg.C. m/W and ground temperature 300C.
	





A
	





-------------
	





-------------
	-------------

	20.1
	One three-phase circuit per trench.
	
A
	
-------------
	
-------------
	-------------

	20.2
	Two three-phase circuit 450mm spaced per trench.
	
A
	
-------------
	
-------------
	-------------

	21
	Maximum continuous current carrying capacity per conductor when drawn into pipes or ducts at a depth of 1000mm. Assume g = 1.2 deg.C. m/W and ground temperature 300C.
	





A
	





-------------
	





-------------
	-------------

	21.1
	One three-phase circuit.
	A
	-------------
	-------------
	-------------

	21.2
	Two three-phase circuit 450mm spaced.
	A
	-------------
	-------------
	-------------

	22
	Maximum continuous current carrying capacity per conductor when installed in air at an ambient temperature 40o.C One 3-phase circuit
	




A
	




-------------
	




-------------
	-------------

	23
	Screen loss per 1,000 m of 3 phase circuit at normal working voltage and frequency and at maximum current ratings given in Item 20.1
	




kW
	




-------------
	




-------------
	-------------

	24
	Minimum insulation resistance at 20o C per 1,000 m of one conductor to Screen, the remaining conductors being connected to the Screen 
	




Mohm
	




-------------
	




-------------
	-------------

	25
	Earth fault short circuit current carrying capacity when cable is loaded as in item 20.1 before S/C and conductor temperature 90oC
	



kA
	



-------------
	



-------------
	-------------

	25.1
	Rating of copper screen per core:-

a) 1 sec.

b) 3 sec.

c) Final screen temperature
	kA

kA

oC
	-------------

-------------

-------------
	-------------


-------------

-------------
	-------------
-------------
-------------

	26
	Conductor short circuit current permissible when S/C occurs at conductor temp. of 90oC. for a period of:-

0.2 Seconds

0.4 Seconds

0.6 Seconds

0.8 Seconds

1.0 Seconds

2.0 Seconds

3.0 Seconds

Final conductor temperature
	kA

kA

kA

kA

kA

kA

kA

oC
	-------------

-------------

-------------

-------------
	-------------

-------------

-------------

-------------
	-------------

-------------

-------------

-------------

	27
	Maximum dielectric stress at nominal voltage:-
	
	-------------
	-------------
	-------------

	27.1
	At conductor screen
(assumed smooth)
	
MV/m
	
-------------
	
-------------
	-------------

	27.2
	At core screen
	MV/m
	-------------
	-------------
	-------------

	28
	Impulse withstand voltage:-

(a) positive 1.2/50 wave 

(b) negative 1.2/50 wave
	kVP

kVP
	-------------
	-------------
	-------------

	29
	Partial discharge voltage
Guaranteed maximum discharge
	kV


pC
	-------------
	-------------
	-------------

	30
	Tan ( measurment as a function of voltage:-
At 0.5 Uo.

At Uo.

At 2.0 Uo.

Max. difference between 0.5Uo and 2.0Uo.
	
	-------------

-------------
	-------------

-------------
	-------------

-------------

	31
	Tan ( measurement as a function of temperature:-
At ambient temperature.

At max. operating temperature (90oC).
	
	-------------
	-------------
	-------------

	32
	How the information will appear on the outer sheath.
	
	
-------------
	
-------------
	-------------

	33
	Is the length in meter along the cable appear at each meter.
	

Y/N
	

-------------
	

-------------
	-------------

	34
	Number of years experience in the production of the type and size of cables specified herein
	
	


-------------
	


-------------
	-------------

	35
	Has ageing test been performed in accordance with the applicable IEC standards
	


Y/N
	


-------------
	


-------------
	-------------

	36
	Name and location of testing laboratories.
	
	
-------------
	
-------------
	-------------


SCHEDULE e
DRAWINGS, CATALOGUES, SAMPLES, MAINTENANCE INSTRUCTIONS AND 
JOINTING INSTRUCTIONS DRAWINGS

All drawings shall be to scale and fully detailed. All important dimensions shall be shown and the material of which each part is constructed shall be shown. Drawings for approval shall be initially submitted in duplicate as prints. Any further prints required by the Engineer shall be supplied on request.

After approval of the drawings the Supplier shall, if required, supply further prints of which one may be required to be a "Velograph" print on tracing cloth or plastic film.

All detail drawings submitted for approval shall be to an approved scale preferably not less than 1:20.

The Supplier shall submit detailed drawings showing all relevant dimensions, cross sections etc. of each item tendered for as detailed in Schedule 'G1' and shall list the drawings submitted hereunder.

	Tenderer's Drawing
	Description

	…………………….……….
	………………………….………………….……….

	…………………….……….
	………………………….………………….……….

	…………………….……….
	………………………….………………….……….

	…………………….……….
	………………………….………………….……….

	…………………….……….
	………………………….………………….……….

	…………………….……….
	………………………….………………….……….

	…………………….……….
	………………………….………………….……….

	…………………….……….
	………………………….………………….……….

	…………………….……….
	………………………….………………….……….

	…………………….……….
	………………………….………………….……….

	…………………….……….
	………………………….………………….……….

	…………………….……….
	………………………….………………….……….


Detailed drawings corresponding to all drawings submitted by the Tenderer with his Tender, and for those items in Schedule 'G' which are included in the Contract shall be submitted by the Supplier for approval within one month from the Commencement date see Schedule 'B'.

SCHEDULE e – continued
DRAWINGS, CATALOGUES, SAMPLES, MAINTENANCE INSTRUCTIONS AND JOINTING INSTRUCTIONS DRAWINGS

CATALOGUES

A set of the Cable Manufacturer's catalogues dealing with the cables offered shall be attached to the Tender.

SAMPLES

The supplier shall submit for approval, samples of materials or fittings as required from time to time by the Engineer.

At the conclusion of the work the Supplier shall if required by the Engineers provide samples of all cables supplied and the samples shall be mounted on a board in an approved manner.

MAINTENANCE INSTRUCTIONS

Where the equipment supplied is subject to maintenance during service the supplier shall submit for approval a draft of the recommended Maintenance Instructions. After approval the Supplier shall supply any further copies required by the Engineer. These Maintenance Instructions shall be provided before the taking over of any part of the equipment.

sCHEDULE f1
STANDARDS

The Tenderer shall list the standard specifications to which the main items of tendered equipment are designed and manufactured.  

	Equipment
	National Standard
	English Title

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	


sCHEDULE f2
ALTERNATIVE STANDARDS PROPOSED BY TENDERER

The British Standards and IEC Standards incorporated in this Specification are given below.  They include all current amendments also other British Standards to which reference may be made in the contents.  Tenderers must quote below any alternative standards they propose to adopt in the event of being awarded a Contract.

	BS
	Item
	Alternative proposed by Tenderer

	223  :  1956
	High Voltage Bushings
	………………………………

	443  :  1969
	Tests on the zinc coating of galvanised steel armouring wires
	
………………………………

	729  :  1971
	Zinc coatings on Iron and steel articles
	………………………………

	801  :  1953
	Lead alloy for cable sheathing 
	………………………………

	903  :  1971
	Methods of Testing Vulcanised Rubber 
	………………………………

	923  :  1980
(IEC 60060 - 1/4)
	Impulse testing 
	
………………………………

	IEC 60502
	Extruded Dielectric Insulated Power Cables 1 kV - 30 kV 
	
………………………………

	1442 :  1969
	Galvanised steel armouring wires.
	………………………………

	1858 :  1973
	Bitumen-Base filling compounds for electrical purposes.
	
………………………………

	2782 :  1970
	Methods of Testing Plastics.
	………………………………

	6234 :   1969
	Polyethylene insulation and sheath of electric cables.
	
………………………………

	6360 :   1981
(IEC 60228)
	Copper conductors in insulated cables and cords.
	………………………………

	6480 :   1969
(IEC 60055)
	Impregnated paper insulated cables
	………………………………

	6746 :   1969
(IEC 60811)
	PVC for cable insulation and sheathing.
	………………………………

	6622 :   1985
	Cables with XLPE or EPR insulation for rated voltages from 3800/6600V to 19000/33000V
	


………………………………


sCHEDULE f2 – CONTINUED
ALTERNATIVE STANDARDS PROPOSED BY TENDERER

	BS
	Item
	Alternative proposed by Tenderer

	VDE 0273/87
	Crosslinked Polyethylene insulated Cables Nominal Voltages Uo/U 6/10, 12/20 and 18/30 kV
	

…………………………………..

	ICEA S-66-524
NEMA 7-1982
	Cross-Linked Thermo-setting Polyethylene-insulated Wire and Cable for the Transmission and Distribution of Electrical Energy
	


…………………………………..


schedule G
deviations from specification

(a) It will be assumed that the plan offered will conform to the Specification in all respects unless deviations are mentioned in this Schedule.  

(b) The Purchaser may waive any minor informality, non-conformity or irregularity in an offer that does not constitute a material deviation provided such waiver does not prejudice or affect the ranking of any Tenderer.  Major deviations in the opinion of the Engineer will render the bid non‑responsive.  
(c) If, upon completing manufacturing and during inspection and delivery process, it is found that certain items that are required and clearly stated in the technical specifications but not included in the final product are not declared in the schedule of deviations (K), then the technical specifications shall prevail and the manufacturer shall be responsible for adding these items to fulfill all requirements called for in the specification at his own cost unless otherwise agreed with the Engineer.

schedule H
transport facilities

General
It shall be the responsibility of the Contractor to arrange for the shipment of all equipment from the country of origin to the Port of Entry in the Hashemite Kingdom of Jordan.  

Sea freight

When equipment is shipped by sea it must be consigned to the Port of Aqaba.  

Transfer of equipment from ship to shore is normally done by mobile crane or ships derricks, otherwise by lighters which have a maximum capacity of 500 tonnes.  Unloading from the lighter to the quay is limited to a maximum lift of 10 tonnes by means of a mobile crane.  

Roll-on and roll-off facilities are also available for containerised goods.  Containerised goods may be consigned to Amman for customs clearance.  

For special heavy loads a ‘Z’ craft is available in the harbour onto which a heavy trailer can be manoeuvred from a special base constructed for this purpose.  

Trailers with a loading capacity of up to 40 tonnes are available in Jordan and therefore the limit of weight which can be handled depends entirely on the capacity of the ships derricks.  

Transport from the Port normally is on 340 km of rough road although there is a rail head at Ma’an (100 km north of Aqaba).  The rail gauge is 1050 mm and the rail company possesses eighteen “flats” each with a maximum capacity of 15 tonnes.  

Airfreight

When airfreight of equipment is authorized it must be consigned to Queen Alia International Airport, Amman.  

Any goods to be shipped by air may be made by eligible airlines in accordance with Clause 1.4 of Instructions to Bidders.  The Jordanian International Airport is Amman’s Queen Alia International Airport (QAIA). The Royal Jordanian airlines have direct services to this airport.  

�EMBED Equation.3���





�EMBED Equation.3���








* 	Unless otherwise specified.


*	Materials and apparatus shall be tested at the Maker's Works in accordance with the appropriate National/International Specifications or equivalent specifications which may be applicable.





30

[image: image3.wmf]ú

û

ù

+

ê

ë

é

500

500

2

1

L

L

_1453367713.unknown

_1453367715.unknown

