[image: image5.png]



the hashemite kingdom of jordan
the jordanian electric power company limited
Specification JEP 22/2026
tender document for

 12& 36kv SILICONE rubber COMPOSITE tension INSULATORS
	Tenderer's Name:
	________________________

	Address:
	________________________

	Closing Date:
	________________________

	Closing Time:
	________________________


january   2026
CONTENTS

7

1.
scope of work

7

1.1
Definite work

8

2.
sITE AND DESIGN PARTICULARS

8

2.1
Particulars of system

8

2.2
Electrical design data

8

2.2.1
System particulars

8

2.2.2
Equipment withstand voltage

9

2.2.3
Outdoor bushing and insulator creepage distances

9

2.2.4
Cable box clearances

9

2.2.5
Minimum clearance from live metal to oil pipework (including conservator and pressure relief devices on transformers)

10

2.2.6
Auxiliary power supplies

10

2.3
Site conditions

10

2.3.1
General

10

2.3.2
Elevation

10

2.3.3
Earthquakes

10

2.3.4
Snow

10

2.3.5
Hail

11

2.3.6
Air temperature (Degrees Centigrade)

11

2.3.7
Rainfall amount (millimeter)

11

2.3.8
Relative humidity (%)

11

2.3.9
Mean wind speed (m/s)

12

2.3.10
Clouds “oktas”

12

2.3.11
Fog “visibility 1 km or less”

12

2.3.12
Dust “visibility 1 km or less”

12

2.3.13
Thunderstorms

13

3.
GENERAL TECHNICAL CLAUSES

13

3.1
Standards

13

3.2
Design and standardization

14

3.3
Galvanizing

15

3.4
Copper conductors

15

3.5
Aluminium and aluminium alloys

15

3.6
Labels and identification plates

17

3.7
Bolts and nuts

17

3.8
Cleaning and painting

18

3.8.1
External surfaces at works

18

3.8.2
Internal surfaces

18

3.9
Insulating oil and gas

19

3.10
Prevention of acidity

19

3.11
Fire precautions

19

3.12
Corona and radio interference

19

3.13
Locking devices and padlocks

19

3.14
Tools

19

3.15
Erection marks

20

3.16
Operating and maintenance instructions

20

3.17
Spare parts

20

3.18
Manufacturing experience and qualifications

20

3.19
Quality Assurance system

21

4.
SILICONE COMPOSITE INSULATORS

21

4.1
Standards Referred To

21

4.2
Design of Insulators

21

4.2.1 Core

21

4.2.2 Housing

22

4.2.3 End Fittings

22

4.3
Electrical Design

22

4.4
Mechanical Design

22

4.5
Sample Silicone Composite Insulators

22

4.6
Tolerances On Dimensions

23

4.7
Warranty

23

4.8
Identification

23

4.9
Packing

24

5 
INSPECTION AND TESTS

24

5.1
General

24

5.2
SILICONE RUBBER COMPOSITE TENSION INSULATORS

24

5.2.1
Design Test

25

5.2.2
Type Tests

25

5.2.3
Sample Tests

26

5.2.4
Routine Tests

26

5.2.5
Ageing Test

27

SCHEDULE a - ITEMS OF THE CONTRACT

27

SCHEDULE B - TIME DELIVERY PERIODS  

28

SCHEDULE C - MANUFACTURERS AND PLACES OF MANUFACTURE, TESTING AND INSPECTION

SCHEDULE D - technical data
29
32

SCHEDULE e1 -  DRAWINGS

34

SCHEDULE e2 - DRAWINGS and MAINTENANCE INSTRUCTIONS

34

sCHEDULE f - STANDARDS

36

SCHEDULE G1 - list of equipment with prices

37

schedule g2 -  quantities with prices

Error! Bookmark not defined.

SCHEDULE h - SUMMARY OF TOTAL FIRM PRICES

Error! Bookmark not defined.

schedule j - recommended spares for OVERHEAD LINE EQUIPMENT

39

schedule K - deviations from specification

40

schedule l - list of special tools and equipment required for maintenance purposes

41

schedule n - transport facilities

42

schedule  t – TEST CERTIFICATEs AND REFERENCE LIST



LIST OF ABBREVIATIONS

	BS
	British Standards

	IEC
	International Electrotechnical Commission

	JEPCO
	The Jordanian Electric Power Company Limited


Form oF Tender
THE JORDANIAN ELECTRIC power COMPANY LIMITED
TENDER FOR CONTRACT NO JEP 22/2026                                                              12 & 36KV SILICONE RUBBER COMPOSITE TENSION INSULATORS
(Tenderers are required to fill up the blank spaces in this Tender Form and Appendix)

The General Manager

The Jordanian Electric Power Company Limited

PO Box 618

Amman 11118

The Hashemite Kingdom of Jordan

1.
Having examined the Drawings, Conditions of Contract, Specification and Schedules for the execution of the above-named Goods, we, the undersigned, offer to execute, complete and remedy defects in the whole of the said Goods in conformity with the said Drawings, Conditions of Contact, Specification and Schedules for the sum of 
…………

(Figures…………..………………….)
or such other sum as may be determined in accordance with the said conditions.

2.
We agree to abide by this Tender for the period of 120 days from the date fixed for receiving the same and it shall remain binding upon us and may be accepted at any time before the expiration of that period.  

3.
We undertake if our Tender is accepted to complete and deliver the whole of the Goods comprised in the Contract within 
…………… week(s) subject to the said Conditions.

4.
If our Tender is accepted we will obtain the guarantee of an Insurance Company or Bank or other sureties (to be approved by you) to be jointly and severally bound with us in a sum not exceeding 10 per cent of the above named sum for the due performance of the Contract under the terms of a Bond to be approved by you.  

We propose the following Bank or Insurance Company as surety (or sureties) in this respect:

(
)

(
)

(
)

5.
Unless and until a formal Agreement is prepared and executed, this Tender, together with your written acceptance thereof, shall constitute a binding Contract between us.

6.
We undertake to provide a defects guarantee period as stated in Clause 15 of the conditions of contract for each section of the Plant from the date of delivery to the Port of Aqaba, or such other destination that may be stated in the Contract.  

7.
We understand that you are not bound to accept the lowest or any Tender you may receive.

8.
Tenderers must give details of their representative or associated companies in the Hashemite Kingdom of Jordan who will deal with this Contract if it is awarded to the Tenderer:

Name and Full Address of Representative:



Telephone Number



Fax Number



Telex Number



9.
APPENDIX TO TENDER

	
	Clause
	

	Time for completion
	10.1
	
 weeks

	Amount of Bond or Guarantee
	 7.1
	10% of Contract sum 


	
	11.1
	Full replacement value +
 10%

	Amount of reduction per week of delay
	23.1
	1% 

 of Contract Price

	Maximum reduction
	23.1
	10% 

of Contract Price

	Defects Liability Period
	15.2
	


	Use of Goods assumed
	
	

24 hours per day

	Name and address of Tenderer’s Bank
	
	



Dated this 

day of 


200…

Signature 

in the capacity of 


Duly authorized to sign tenders for and on behalf of 


Witness

Address


Occupation

1.
scope of work

1.1
Definite work

The works shall comprise the design, manufacture, testing and delivery to the Port of Aqaba, The Hashemite Kingdom of Jordan of the equipment listed in this Specification, equipment in accordance with the Conditions of Contract at prices stated in the Schedule of this Specification, together with the provision of certain specified spares.  

	Item No.
	Description
	Quantity

	1.
	12 kV, Silicone rubber composite tension insulator complete with end fitting (Ball 16mm – Socket 16mm with stainless steel “W” clip)
	1,000

	2.
	36 kV, Silicone rubber composite tension insulator complete with end fitting (Ball 16mm – Socket 16mm with stainless steel “W” clip)
	5,000


NOTES:
· Documents to be submitted as an integral part of the offer, and to be evaluated with the Tender:

1. Full technical details, drawings and catalogues of the items required here in.

2. Type test certificates from any European STL member laboratory (KEMA, CESI, and IPH) or equivalent. 
3. 1,000 hours salt fog Tracking and erosion test for silicone rubber housing shall be According to the latest edition of IEC 62217-2012.

4. Fully detailed reference list with contact details.

5. ISO certificate and any other documents that may assist in the evaluation.
· Two Non-returnable tension insulator Samples identical to the design offered, shall be submitted with the Tender on the specified closing date. The representative samples shall be thoroughly examined and shall undergo mechanical and electrical tests. Failure to deliver the samples or failure of the samples to meet the mechanical and electrical Specifications set out in this Document will entitle the Purchaser to reject the Tender. 
· All above items shall be provided with a bar code of 128 type C that represents the primary and secondary number of these items, as shown in the table below:
	Item No.
	Item Code

	1.
	00651601

	2.
	00661601


2.
sITE AND DESIGN PARTICULARS

2.1
Particulars of system

The following are the particulars of the systems on which the equipment covered by the Specification shall operate:-
i. 33 kV, 3-phase at a frequency of 50 Hz with the neutral point resistance earthed.  

ii. 11 kV, 3-phase at a frequency of 50 Hz with the neutral point solidly earthed.  

iii. 415 volts 3-phase and neutral at a frequency of 50 Hz with the neutral point solidly earthed.  

2.2
Electrical design data

2.2.1
System particulars

	Nominal system voltage between phases
	
kV
	
33
	
11
	
0.415

	Highest system voltage
	kV
	36
	12
	0.440

	System fault level
	kA
	31.5
	25
	50*

	Earthing system
	

	Resistance earthed
	Solidly
earthed
	Solidly
earthed

	System frequency
	Hz
	50
	50
	50


2.2.2
Equipment withstand voltage

	i.

	Outdoor bushings, insulators and pole mounted transformers

	
	Impulse withstand voltage (1.2/50µs wave) peak
	
kV
	
250
	
95
	
-

	
	Power frequency withstand voltage
	
kV
	
95
	
38
	
-

	ii.

	All other equipment excluding pole mounted transformers

	
	Impulse withstand voltage (1.2/50µs wave) peak
	
kV
	
170
	
75
	
-

	
	Power frequency withstand voltage
	
kV
	
75
	
28
	
-


2.2.3
Outdoor bushing and insulator creepage distances

	Minimum creepage distance
	mm
	1089
	400
	-

	Protected creepage distance
	mm
	545
	160
	


2.2.4
Cable box clearances

The minimum cable box clearances under compound or oil shall be as follows:-

	Nominal system voltage
	kV
	33
	11
	Below 1

	Minimum clearance between phases
	
mm
	
125
	
45
	
20

	Minimum clearance phase to earth
	
mm
	
100
	
32
	
20

	Minimum creepage distance phase to earth over cable surface
	

mm
	

250
	

125
	

26

	The minimum cable box clearances in air-filed, air-insulated boxes, live metal to live metal and unshrouded shall be as follows:-

	Nominal system voltage
	kV
	33
	11
	

	Minimum clearance between phases
	
mm
	
356
	
178
	

	Minimum clearance phase to earth
	
mm
	
222
	
115
	

	Minimum creepage distance phase to earth over cable tail surface
	

mm
	

800
	

450
	

	The minimum cable box clearance in air-filled boxes with shrouded insulation termination is as follows:-

When this type of termination is used the dimensions will be based on the termination manufacturers recommendations and be subject to approval by the Engineer.  


2.2.5
Minimum clearance from live metal to oil pipework (including conservator and pressure relief devices on transformers)

	Highest system voltage
	kV
	36
	12

	Minimum clearance
	mm
	485
	250

	Apart from the clearances detailed under this item, no phase or earth clearances are specified for transformers where an impulse voltage test level is specified.  


2.2.6
Auxiliary power supplies

	Supply voltage for auxiliary equipment
	i.
400 volt, 3 phase and Neutral 50 Hz

	
	ii.
110 volts DC 2 wire


2.3
Site conditions

2.3.1
General

The site conditions shall be assumed to be as follows for the purposes of Tender preparation.  

2.3.2
Elevation

766 meters above sea level - Amman Airport at which all the climatic observations used were taken by the Jordanian Ministry of Transport Meteorological Department.  

2.3.3
Earthquakes

Amman is classified as Seismic Zone 2.  

2.3.4
Snow

Snowfall in cm at Locations in the Amman Area in 10 years 1972-1982.  

	Area
	No of days of snowfall/year
	Greatest depth of snow (cm)

	Wadi Dhuleil
	1-04
	10

	Amman Airport
	1-13
	30

	Jordan University
	1-13
	60

	Naur
	1-13
	45

	Ma
	1-04
	25


2.3.5
Hail

Not a normal occurrence but occurs on average 3.2 days per year.  

	Station: Amman Airport
	31 deg 59 min NORTH
35 deg 59 min EAST
766 m above sea 

	Period: 1923 - 1985
	


2.3.6
Air temperature (Degrees Centigrade)

	
	JAN
	FEB
	MAR
	APR
	MAY
	JUN
	JUL
	AUG
	SEP
	OCT
	NOV
	DEC
	YEAR-LY

	Mean monthly
	
7.9
	
9.
	
11.7
	
15.9
	
20.5
	
23.6
	
25.1
	
25.4
	
23.5
	
20.4
	
14.9
	
9.8
	
17.3

	Mean daily max
	
12.4
	
13.8
	
17.4
	
22.5
	
27.8
	
30.9
	
31.9
	
32.4
	
30.7
	
27.2
	
20.6
	
14.5
	
23.5

	Mean daily min
	
3.5
	
4.2
	
6.1
	
9.3
	
13.3
	
16.3
	
18.2
	
18.3
	
16.2
	
13.6
	
9.3
	
5.1
	
11.1

	Absolute max
	26.3
	29.4
	32.5
	39.2
	40.6
	42.8
	42.4
	42.8
	40.6
	37.4
	.8
	27.3
	42.8

	Absolute min
	-7.5
	-6.5
	-3.9
	0.0
	3.0
	7.8
	11.0
	11.5
	8.9
	4.9
	-3.2
	-5.3
	-7.5

	Design ambient temperature is 45 degrees centigrade


2.3.7
Rainfall amount (millimeter)

	Mean monthly
	
64.5
	
63.9
	
44.7
	
16.1
	
3.7
	
0.03
	
TR
	
TR
	
0.4
	
5.8
	
28.6
	
48.6
	
276.3

	Max amount in a month
	

235.2
	

190.8
	

168.7
	

151.3
	

30.6
	

1.1
	

TR
	

TR
	

15.4
	

54.6
	

136.8
	

179.8
	

476.5

	Max amount in one day
	

75.6
	

80.0
	

66.2
	

52.4
	

24.1
	

1.1
	

TR
	

TR
	

15.4
	

40.5
	

79.4
	

73.6
	

80.0


2.3.8
Relative humidity (%)

	Mean monthly
	
70.0
	
67.0
	
60.0
	
50.0
	
39.0
	
37.0
	
40.0
	
43.0
	
47.0
	
46.0
	
56.0
	
68.0
	
52.0

	Max relative humidity reaches 100 per cent especially during rainy intervals and night, while min relative humidity drops to less than 10 per cent on some occasions especially during Khamsinic conditions (22 March - 10 May).  


2.3.9
Mean wind speed (m/s)

	Direction (deg)
	
227
	
241
	
251
	
254
	
275
	
276
	
278
	
282
	
284
	
267
	
226
	
222
	
264

	Mean monthly
	
3.2
	
3.3
	
3.4
	
3.6
	
3.3
	
3.6
	
3.9
	
3.4
	
2.6
	
2.2
	
2.4
	
2.9
	
3.2

	Max wind gust
	

35
	

28
	

30
	

31
	

24
	

22
	

19
	

17
	

17
	

26
	

26
	

34
	

…..


2.3.10
Clouds “oktas”

	Mean amount
	
3.8
	
3.5
	
3.4
	
3.2
	
1.9
	
0.6
	
0.3
	
0.3
	
0.7
	
1.5
	
2.6
	
3.4
	
2.1

	No cloudy days
	

4.7
	

3.1
	

3.8
	

2.5
	

0.7
	

0.0
	

0.0
	

0.0
	

0.0
	

0.3
	

1.0
	

3.6
	

19.5


2.3.11
Fog “visibility 1 km or less”

	Mean no of days
	
1.5
	
0.7
	
0.4
	
0.2
	
0.0
	
0.0
	
0.0
	
0.0
	
0.0
	
0.1
	
0.3
	
0.7
	
3.9

	Max number of days with fog 11 days per year


2.3.12
Dust “visibility 1 km or less”

	Mean no of days
	
0.4
	
0.1
	
0.6
	
0.2
	
0.2
	
0.0
	
0.0
	
0.0
	
0.0
	
0.0
	
0.2
	
0.1
	
1.7

	Max number of days with dust 6 days per year


2.3.13
Thunderstorms

	Mean no of days
	
0.4
	
0.4
	
1.3
	
0.8
	
0.6
	
0.0
	
0.0
	
0.0
	
0.4
	
1.2
	
1.1
	
0.4
	
6.6

	Max number of days with thunder storms 17 days per year


3.
GENERAL TECHNICAL CLAUSES

3.1
Standards

Although  American, British or IEC standards for workmanship, material and equipment have been selected in these Specifications as a basis of reference, standards and specifications of other countries and recommendations of  other standard international organisations will be acceptable provided they are substantially equivalent to, or higher  than, the designated standards and provided furthermore that the Supplier submits for approval details of the specifications heproposes to use.

When IEC recommendations or national standards are referred to the Edition shall be that current at the date of Tender, together with any amendments issued to that date.  

If requested by the Engineer, the Contractor shall supply at his own expense one copy in English and one in the original language of any national standards which are applicable to the Contract.  

3.2
Design and standardization

The Goods shall be designed to facilitate inspection, cleaning and repairs, and for operation in which continuity of service is the first consideration. All apparatus shall be designed to ensure satisfactory operation under the atmospheric conditions prevailing at the Sites and under such sudden variations of load and voltage as may be met with under working conditions on the system , and short circuits, including those due to faulty synchronising within the rating of the apparatus.

The design shall incorporate every reasonable precaution and provision for the safety of all those concerned in the operation and maintenance of the Goods and of associated works supplied under other Contracts.

All material used shall be of the best quality and of the class  most suitable for working under the conditions specified and shall withstand the variations of  temperature and atmospheric conditions arising under working conditions without distortion or deterioration or the setting up undue stresses in any part, and also without affecting the strength and suitability of the various parts for the work which they have to perform. No welding, filling or plugging of defective parts will be permitted without the sanction in writing of the Engineer.

Corresponding parts liable to renewal shall be interchangeable. When required by the Engineer, the Supplier shall demonstrate this quality.

All apparatus shall operate without undue vibration and with the least practicable amount of noise. 

Cast iron shall not be used for chambers of oil-filled apparatus or for any part of the equipment which is in tension or subject to impact stresses except where it can be shown that service experience has been satisfactory with the grade of cast iron and the duty proposed.

Operating boxes, kiosks, cubicles and similar enclosed compartments forming part of auxiliary equipment shall be adequately ventilated to restrict condensation, and,where required  by  the  Engineer, suitable low-temperature heaters shall be provided. All contactor or relay coils and other parts shall be suitably protected against corrosion.

All outdoor apparatus, including bushing insulators and fittings shall be so designed as to avoid pockets in which water can collect.

The underside of all tanks shall be ventilated in an approved manner to prevent corrosion.

Accessible  means shall be provided for the easy lubrication of all  bearings  and  where necessary, of any mechanism or moving part. Grease lubricators shall be fitted with hexagon nipples.

All mechanisms shall, when  necessary, be constructed of stainless steel, brass or gunmetal to prevent sticking due to rust or corrosion.

All taper pins used in any mechanism shall be of the split type.

The busbars, connections, isolators, fuses, contacts, cable boxes,  trunking connections etc,. which form part of the Contract Works shall not exceed the temperature rise values specified in the relevant IEC publication or equivalent national standard. 

All connections and contacts shall be of ample section and surface for carrying continuously the specified currents without undue heating, and shall be secured by bolts or set screws of ample size,  fitted  with locking devices of approved type and material.

All rubbing or wearing surfaces shall be machine surfaced. Joints employing a gasket material shall be so consturcted that the packing is  maintained under sufficient compression in all parts,  so that an efficient joint can be made  without the use of jointing compounds.  Gasket material shall be of the minimum thickness necessary and of approved composition.

All apparatus shall be designed to obviate  the  risk  ofaccidental  short circuit  due to animals,  birds, and vermin. Openings in ventilated enclosures shall be so constructed to prevent the entry of vermin and insects.

3.3
Galvanizing

Galvanizing shall be applied by the hot dipped process.  The preparation for galvanizing and the galvanizing process shall not adversely affect the mechanical properties of the material being coated.  The zinc coating shall be clean, of uniform thickness and free from defects.  

When zinc spray coating is used, surfaces shall be shot blasted before spraying.  

Drilling, punching, cutting, bending and removal of burrs shall be completed before galvanizing/zinc spray coating.  

The average thickness of the zinc coating shall be equivalent to not less than 0.6 kg/m2 of zinc for all surfaces, except steel wires.  

The thickness of the zinc coating for steel wires shall be in accordance with a national standard and shall be approved by the Engineer.  

Material on which galvanizing has been damaged shall be re-dipped unless, in the opinion of the Engineer, the damage is local and can be repaired by applying a coat of galvanizing repair paint.  Where such a repair is authorized, the damaged area shall be cleaned by wiping with clean rags saturated with mineral spirits or xylene followed by wire brushing.  After wire brushing, the area shall be re-cleaned with solvent to remove residue and shall be given a minimum of two coats of zinc rich paint in accordance with the manufacturer’s instructions.  

Samples selected by the Engineer of all galvanized material shall be subjected to the galvanizing tests set out in the appropriate material standard (eg BS 443/BS 729).  

Sherardizing or other similar processes shall not be used unless expressly approved by the Engineer.  

Surfaces in contact with oil shall not be galvanized or cadmium plated.  

3.4
Copper conductors

All copper conductors shall be composed of high conductivity electrolytic copper having a conductivity of not less than 99.9 per cent of the International Agreed Copper Standard (IACS).  

3.5
Aluminium and aluminium alloys

Aluminium shall be of high commercial quality. The composition, including the percentage and nature of any impurities, shall be stated in the schedules.  

All aluminium alloys shall be of approved compositions as stated in the schedules.  

Aluminium and aluminium alloy castings shall be sound and free from porosity.  

3.6
Labels and identification plates

All equipment shall be clearly and permanently labelled, to the approval of the Engineer, in English, unless otherwise specified.  Where labels are provided in diagrammatic form, any inscription shall be in English unless otherwise specified.  

A label shall be permanently fixed to each item of equipment in a clearly visible position stating:  

Property of The Jordanian Electric Power Co Ltd
Year of Manufacture

All control and relay panels, marshalling boxes, kiosks, distribution boxes and other cubicles shall be labelled to show the circuit with which it is associated.  These labels shall be fitted to the front and back of all equipment.  

Labels, number plates and their fixing screws, for outdoor use, shall be of stainless steel or other corrosion resistant material.  Where the use of vitreous enamelled labels is approved, the whole surface including the back and edges shall be properly covered and protewasshall be provided front and back on the fixing screws.  

The materials of the labels and number plates, for indoor and outdoor use, shall be approved by the Engineer and shall be fixed so as to prevent buckling due to temperature and humidity variations.  

Danger notices shall have red lettering on a white background and shall be in English and Arabic.  

Unless otherwise approved by the Engineer, all other labels and number plates shall have black inscriptions on a white base colour.  

Labels for similar equipment shall be of uniform appearance and the dimensions and size of letter shall be to the approval of the Engineer.  
Each equipment shall be marked with its function, manufacturer's name or trade mark and the code type number together with the batch or serial number.

Each detachable unit  shall be either marked so as to enable it to be identified with the parent equipment, or else marked with the manufacturer's name and type number or code number and where definable, its function.

Each Unit and sub-unit mounting position shall be marked to indicate  the type of unit or sub-unit to be located in that position. Addmarkings may be required for apparently identical units or sub-units having different pre-set characteristics.

Component reference numbers shall be marked adjacent to the component. Where this is impossible, components shall be identifiable from the drawings provided by the Contractor.

The following shall be marked in all instances:-

(a)
Fuse. The rating and circuit identification of each fuse shall be marked adjacent to the fuse base.

(b)
Control and Indicating Devices. The function  of each control and indication device shall be marked. The caption and its arrangement shall be subject to the approval of the Engineer.

(c)
Pre-set Controls. The circuits reference and if possible, the function, shall be marked adjacent to each pre-set control in a position where it will be clearly visible while the adjustment is being made.

(d)
Connectors. The diagram reference number shall be marked on, or adjacent to each connector.

(e)
Test Points shall be individually marked with the diagram reference number.

All junction boxes shall include a record pasted inside the lid showing the terminal allocation.

Each terminal of a screw type terminal block shall bear the identification marking either on the body of the block, or adjacent to it. All other terminal blocks shall be marked with their circuit designations and rows shall be marked to identify each connection to the approval of the Engineer.

All wiring shall be identifiable by an approved colour code, ferrules marked with the nomenclature adopted for these conductors, on the manufacturer's diagrams, or by circuit reference at the terminals.

3.7
Bolts and nuts

All bolts, studs, screw threads, pipe thread, bolt heads and nuts shall be of ISO metric standard type.  

Except for small wiring, current carrying terminal bolts or studs, for mechanical , shall not be less than 6 mm in diameter.

All nuts and pins shall be adequately locked.

Wherever possible bolts shall be fitted in such a manner that in the event of failure of locking resulting in the nuts working loose and falling off, the bolt will remain in position.

All bolts, nuts and washers placed in outdoor positions shall be treated to prevent corrosion of the threads and electrolytic action between dissimilar metals.

Where bolts are used on external horizontal surfaces where water can collect, methods of preventing the ingress of moisture to the threads shall be provided.

Each bolt or stud shall project at least one thread but not more than four threads through its nut, except when otherwise approved for terminal board studs or relay stems.  If bolts and nuts are placed so that they are inaccessible by means of ordinary spanners, special spanners shall be provided.

The length of the screwed portion of the bolts shall be such that no screw thread may form part of a shear plane between members.

Taper washers shall be provided where necessary.

3.8
Cleaning and painting

Before painting or filling with oil, gas or compound, all ungalvanized parts shall be thoroughly cleaned, free from rust, scale, burrs, grease and moisture and all external rough surfaces on casting shall be filled.  

The following minimum painting requirements shall apply to all ferrous parts unless the supplier can show, to the satisfaction of the Engineer, that any alternative he proposes is in all respects equal or superior to the specified requirements:  

3.8.1
External surfaces at works

	All ungalvanized surfaces, other than nuts, bolts and washers, which may be removed for maintenance purposes, for use outdoors
	i.
One priming coat of corrosion inhibiting paint applied immediately after cleaning  

ii.
Two coats of non-glossy, oil- and weather-resisting paint applied after inspection and testing and before despatch

iii.
One finishing coat of glossy oil and water resisting non-fading paint before despatch. 

	Exposed, ungalvanized nuts, bolts and washers which may be removed for maintenance purposes, for use outdoors
	One coat of oil - and weather-resisting, non-fading paint applied.  

	Panels, cubicles, kiosks and apparatus boxes, for use indoors
	Three coats of paint, the colour and finish of the final coat to be to the approval of the Engineer.  

Grey colour is preferable.  


3.8.2
Internal surfaces

	Apparatus
	Painting

	Oil filled chambers and tanks
	One coat of oil resisting varnish or paint

	Kiosks and apparatus boxes for use outdoors
	Three coats of paint, the final coat being an anti-condensation finish coloured white or light grey  

	Cubicles, kiosks and apparatus boxes for use indoors
	Three coats of paint, the final coat being a white or light colour.  


Successive coats of paint shall be easily distinguishable by shade of colour and shall be applied to a clean, dry and properly prepared surface.  Each coat shall be compatible with thprevious coat.  

All paintwork which has bedamaged during transport or erection shall be made good to the approval of the Engineer.  

The colour and shade of all painted external surfaces shall be to the approval of the Engineer.  

3.9
Insulating oil and gas

Unless otherwise specified, sufficient oil or gas shall be supplied to fill all equipment provided under this Contract.  The oil or gas shall be of appropriate type and suitable in all respects for use in the equipment when it is operated under the conditions laid down in this Specification.  The insulating medium used shall comply with the relevant IEC Specification.  

3.10
Prevention of acidity

The design, and all materials and process used in construction of the equipment, shall be such as to reduce to a minimum the risk of development of acidity in the oil or gas.  

3.11
Fire precautions

All apparatus, connections and cabling shall be designed and arranged to minimize the risk of fire and any damage which might be caused in the event of fire.  

3.12
Corona and radio interference

All equipment shall be designed so as to minimize corona or other electrical discharge and radio interference.  
3.13
Locking devices and padlocks

All padlocks, locks and keys required to secure switchgear and other equipment shall be supplied on this Contract.  

Access doors to equipment including circuit breakers, isolating devices, screened enclosures, cubicles and marshalling kiosks and all equipment operating handles, local control and selector switches, valves, switchgear shutters and maintenance positions shall be lockable.  

All padlocks and other locks shall be provided with two identical keys and both the key and the lock shall be impressed with the manufacturer’s serial number.  Except where a master key is specially requested or it has been otherwise agreed, it shall be impossible to open any padlock or lock with the key of any other padlock or lock provided on this Contract.  

When requested, wall mounting lockable cabinets with glazed doors, suitable for accommodation of padlocks and keys whilst not in use, shall be provided.  They shall be mounted in approved positions and shall be labelled in a similar manner to the keys.  The engraving on all labels shall be in accordance with a scheme to be agreed with the Engineer.  

3.14
Tools

The Supplier shall provide any special tools that may be required for making adjustments to equipment during normal operation and maintenance.  These tools are to be of alloy steel and shall be contained in steel boxes, complete with locks and keys.  

All tools shall be stamped in an approved manner for identification purposes.  

3.15
Erection marks

All plant that requires assembly at Site shall have distinguishing marks on it to facilitate erection and to identify the material in relation to drawings, material lists or shipping documents.  All marks shall be legible and easily visible.  Where relevant, erection marks shall be stamped before galvanizing and shall be clearly visible after galvanizing.  

3.16
Operating and maintenance instructions

Operating and maintenance instructions form part of this Contract and shall be provided in accordance with the Conditions of Contract.  

3.17
Spare parts

Particulars of spare parts, which may or may not form part of the Contract at the Engineer’discretion, shall be given in Schedule J.  

3.18
Manufacturing experience and qualifications

The Tenderer shall provide documentary evidence confirming that equipment of an identical design and rating to that offered against this document has been in production for a minimum of 10 years. In addition a list is to be provided with full address, e-mail address and fax number of users with service experience of equipment identical to that offered.

3.19
Quality Assurance system

The supplier must hold ISO 9002 (alternatively ISO 9001) certification of their quality assurance procedures.  Evidence of such certification must be submitted with the Tender.  

Where an equivalent certification to ISO 9002 (alternative ISO 9001) is offered, details of the system, the certification body and the frequency and type of audits, both internal and external, shall be submitted with the Tender.  The equivalent certification shall be subject to review, evaluation and approval by JEPCO or its appointed representative(s).  

4.
12 &36 kv SILICONE RUBBER COMPOSITE TENSION INSULATORS 

4.1
Standards Referred To

The insulator as well as the complete string shall meet the requirements of the latest issue of the following standards:

	IEC 60060-1
	High Voltage Test Techniques
Part 1: General definitions and test requirements

	IEC 60120
	Dimensions of ball and socket coupling of string insulator units

	IEC 60437
	Radio interference tests on high voltage Insulators

	IEC 60471
	Dimensions of clevis and tongue couplings of string insulator units

	IEC 60815
	Guide for the selection of insulators in respect of polluted conditions

	IEC 61109
	Composite insulators for A. C. overhead lines with a nominal voltage greater than 1000 V


4.2
Design of Insulators

The composite insulator consists of three parts: load bearing glass fibre reinforced rod (core), polymeric housing and metallic end fittings.
4.2.1   Core

The mechanical functions are taken over by the insulator core which shall be a glass-fibre reinforced epoxy resin rod of high strength FRP rod( Fibre-reinforced polymer ). Glass fibres and resin shall be optimized regarding mechanical strength and moisture absorption.

The interface formed by rod and housing shall be of a quality to prevent brittle fracture phenomena. ECR-glass fibres, that have a high electrical strength (in comparison with ECR-glass) and equivalent acid resistance,can also be provided.
4.2.2   Housing

The housing shall consist of silicone rubber directly moulded onto the rod. The flash of the seam shall be removed in case of unexceptional appearance.
The silicone rubber shall have excellent UV resistant performance with minimum  thickness of the silicone rubber covering the rod 3 mm. The concentricity of the rod within embeded in the silicone rubber housing has to be proven. This housing protects the core against the environmental influences. To fulfil this duty over an expected life time of more than 30 years, the interface between housing and core shall be chemically bonded.

To achieve an excellent pollution performance and tracking performance of the housing the application of high temperature vulcanizing (HTV) silicone rubber filled with an appropriate amount of aluminium tri hydrate (ATH) shall be preferred.

The shed design shall be in accordance with lEC 60815. A flat, aerodynamic profile is required since the requested insulators under this specification will be installed in desert areas. The shed design shall take into account the better self-cleaning performance of silicone rubber sheds, which is caused by their flexibility. The creepage distance and protected creepage distance shall be as specified in clause 2.2.3 of this specification.

4.2.3   End Fittings

End fittings bear the mechanical load to the core. Considering mechanical values exceeding 80 kN (SML) they should be made of forged steel preferably (high tensile strength quality). The housing shall be extended (During manufacture) over the end fittings for a suitable length to ensure sealing rigidity and continuity of insulation. The overlab are shall be free from defects or gaps.
The fittings shall be attached onto the rod by a compression method process (coaxial or hexagonal compression method) which does not damage the individual fibres of the rod in any way. The required end fittings configuration is shown in the attached drawings. Dimensions of clevis and tongue connection shall be in accordance with lEC 60471.
4.3
Electrical Design

The total creepage distance and the protected creepage distance over the external surface of bushings and insulators shall not be less than the minimum values specified in clause 2.2.3, The protected creepage distance refers to that part of the insulator which is protected against rain at right angles to the axis of the bushing. For tension insulators comprising standard units, the above requirements shall, unless otherwise specified, be met by the addition of an approved number of additional units to the normal assembly.
4.4
Mechanical Design

The strength of insulators shall be such that, when supporting the maximum working load as in service, the factor of safety shall be not less than 2.5. They shall be secured in an approved manner with metal but shall be mounted with suitable interposing materials.

The design shall be such that stresses due to expansion and contraction in any part of the insulator and fittings shall not lead to the development of defects, The design of all insulators shall be such as to achieve an excellent contamination resistant performance.
4.5
Sample Silicone Rubber CompositeTension Insulator
Non-returnable silicone composite tension insulator Samples, one for each of the main items listed in Schedule 'G' and identical to the designs offered, shall be submitted with the Tender on the specified closing date. These representative samples will be thouroughly examined. Failure of the samples to meet the mechanical and electrical Specifications set out in this Document will entitle the Purchaser to reject the Tender.
4.6
Tolerances On Dimensions

In accordance with lEC 61109 the following tolerances are permitted for all dimensions without special request:

· ± (0.04xL+1.5) when L ≤ 300mm

· ± (0.025xL+6) when L > 300mm

4.7
Warranty

The manufacturer shall provide a guarantee for the good performance of the composite insulator. The warranty period shall be 5 years after delivery.

4.8
Identification

The composite Insulator shall be marked In accordance with lEC 61466. All composite Insulators shall carry their identity mark on the insulator not only on the casting.

4.9
Packing

The composite Insulators shall be packed to avoid, damage during transportation. Packing shall be to the approval of the engineer.
5 
INSPECTION AND TESTS

5.1
General

All equipment is subject to inspection by the Engineer at the Manufacturer's Works. Not less than fourteen days notice of all tests shall be given to the Engineer in order that he may present if he so desires. The Supplier shall make the tests specified and any others required by the Engineer to show that the Goods comply with the Specification and with the appropriate Schedules.  The tests shall be made at the Supplier's expense.

No passing of the plant or materials by the Engineer shall relieve the Supplier of his responsibility.  The Supplier shall also be responsible for proper carrying out of all tests of work and of plant and material carried out or supplied by a Sub-contractor to the same extent as if the work, plant or  material were carried out or supplied by the Supplier himself.

If, due to the Goods and/or component materials not complying with this Specification further tests are necessary, the Supplier shall pay all additional costs which may be incurred in re-testing.  

During the execution of the Contract, test specimens, if required by the Engineers, shall be taken from the materials for the purpose of check tests or analyses for testing and forwarded at the expense of the supplier to the Testing Authorities selected by the Engineer. 

One copy of the Supplier's records of all tests shall be given to the Engineer. 

All material which is specified for tests at the Manufacturer's Works shall satisfactorily pass such test before being painted.

All instruments used for the purpose of testing shall be approved and, if requierd, shall be calibrated at the expense of the Supplier by such body as may be approved. 

Where type tests are specified below they shall be carried out in the presence of the Engineer. Alternatively the Supplier shall provide certificates showing that such tests have been carried out satisfactorily on apparatus similar to that being supplied.
5.2
SILICONE RUBBER COMPOSITE TENSION INSULATORS
5.2.1
Design Test

The design tests shall prove the suitability of design, materials and method of manufacturing. These test are prescribed in lEC 61109. It has to be shown that the design of the composite insulator, which is subject of this specification, has passed all of the required tests:

5.2.1.1 Test on interfaces and connections of end fittings

5.2.1.2 Assembled core load-time test

5.2.1.3 Test of housing and shed materials

5.2.1.4 Test of core material

I

5.2.2
Type Tests

The tests are intended to verify the main characteristic (electrical and mechanical) of a composite insulator which is defined by creepage distance, shed inclination, shed diameter, shed spacing, arcing distance, core diameter and the method of attachment of the metal fittings.

The test procedure shall be performed by qualified and well-recognized testing laboratories such as CBLT accredited laboratories.

The electrical and mechanical tests shall be applied to those insulators which have passed the design tests. The electrical tests shall be performed with arcing devices, if they are an Integral part of the insulator type.

Tests are classified as follows:

5.2.2.1 Dry lightning impulse withstand voltage test, according to lEC 60383

5.2.2.2 Wet power frequency test, according to lEC 60383

5.2.2.3 Wet switching impulse withstand voltage according to lEC 60383 for voltage level exceeding 245 kV

5.2.2.4 Mechanical load-line test, according to lEC 61109

5.2.2.5 Radio interference voltage test according to lEC 60437

5.2.3
Sample Tests

The sample tests serve for the verification of typical characteistics of the composite insulator, especially those properties, which can be influenced by deviation or tolerances of manufacturing process and material. The following tests have to be performed on insulators taken at random in propotion with the total quantity (10% max).
5.2.3.1 Verification of dimensions according to lEC 61109

5.2.3.2 Verification of locking system, in case of ball and socket according to lEC 60120, In line with requirements of lEC 60383. For Insulators with clevis and tongue the lEC 60471 is to apply

5.2.3.3 Verification of the mechanical strength SML

5.2.3.4 Galvanizing Test in accordance with lEC 60383

If one insulator of the tested specimen fails to comply with the sample test requirements, re-testing has to be realized according to lEC 61109.

5.2.4
Routine Tests

Each composite Insulator has to be evaluated in the following tests:

5.2.4.1 Visual Examination

This includes the following steps:

· Alignment of fittings according to drawing

· Uniformity of housing surface

· Flash in case of moulded parts

· Sealing system

5.2.4.2 Mechanical Routine Test

Each insulator has to withstand at ambient temperature a tensile load corresponding to at least 50% of the specified mechanical load (SML). The procedure is in accordance with lEC 61109.

5.2.5
Ageing Test

The manufacturer has to submit a test certificate to indicate the performance of a 1000- hour multi-stress salt fog test according to latest edition of lEC 62217. Also, documentations have to be provided to indicate that the test has been passed successfully. The test procedures must be performed by qualified and well-recognized testing laboratories such as STL accredited.
 SCHEDULE a 

ITEMS OF THE CONTRACT FOR THE PURPOSES OF
PAYMENT AND TAKING OVER
	Item No.
	Description
	Quantity

	1.
	12 kV, Silicone rubber composite tension insulator complete with end fitting (Ball 16mm – Socket 16mm with stainless steel “W” clip)
	1,000

	2.
	36 kV, Silicone rubber composite tension insulator complete with end fitting (Ball 16mm – Socket 16mm with stainless steel “W” clip)
	5,000


NOTES:
· Documents to be submitted as an integral part of the offer, and to be evaluated with the tender:

1. Full technical details, drawings and catalogues of the items required here in.

2. Type test certificates from any European STL member laboratory (KEMA, CESI, and IPH) or equivalent. 
3. 1,000 hours salt fog Tracking and erosion test for silicone rubber housing shall be according to the latest edition of IEC 62217-2012.

4. Fully detailed reference list with contact details.

5. ISO certificate and any other documents that may assist in the evaluation.
· Non-returnable tension insulator Samples identical to the design offered, shall be submitted with the Tender on the specified closing date. The representative samples shall be thoroughly examined and shall undergo mechanical and electrical tests. Failure to deliver the samples or failure of the samples to meet the mechanical and electrical Specifications set out in this Document will entitle the Purchaser to reject the Tender. 
· All above items shall be provided with a bar code of 128 type C that represents the primary and secondary number of these items, as shown in the table below:
	Item No.
	Item Code

	1.
	00651601

	2.
	00661601


SCHEDULE B
MANUFACTURERS AND PLACES OF MANUFACTURE,
TESTING AND INSPECTION
(To be completed by the Tenderer)

	Item 

No.
	Description
	Manufacturer
	Place of

Manufacture
	Place of Testing & Inspection*

	1.
	12 & 36 kV silicone rubber composite tension insulators.
	……………..
	……………..
	……………..

	2.
	Raw material of silicone rubber.
	……………..
	……………..
	……………..

	3.
	Glass-fiber reinforced epoxy resin rod.
	……………..
	……………..
	……………..


	SCHEDULE C
technical data
12& 36kV SILICONE RUBBER COMPOSITE TENSION INSULATORS
(To be completed by the Tenderer)

	No.
	Description
	Item No. 1
	Item No. 2

	1.
	1.1 Manufacturer.

1.2 Type number or identification.
	
	---------------

---------------
	---------------

---------------

	2.
	Manufacturing method.
	
	---------------
	---------------

	3.
	Material:

3.1 Core.

3.2 Housing including sheds.

3.3 Sealing.

3.4 End fittings.

3.5 Thickness of zinc coating.
	
	---------------

---------------

---------------

---------------

---------------
	---------------

---------------

---------------

---------------

---------------

	4.
	Electrical data:

4.1 System voltage, Um.

4.2 Impulse withstand voltage, 1.2/50, positive.

4.3 One minute power frequency withstand voltage,           50Hz, wet.

4.4 One minute power frequency withstand voltage, 50Hz, dry.

4.5 Minimum voltage at which corona shall be visible. 
	kV
kV
kV

(kV)

(kV)
	---------------

---------------


---------------


---------------

---------------
	---------------

---------------


---------------


---------------

---------------

	5.
	Mechanical data:

5.1 Specified mechanical load (SML), tension.

5.2 Routine test load.
	(kN)

(kN)
	---------------

---------------
	---------------

---------------

	6.
	Dimensions and drawings:
6.1 Drawing number attached.
6.2 Section length without hardware.
6.3 Diameter of core.
6.4 Number of sheds.
6.5 Diameter of sheds.
6.6 Thickness of silicon rubber for sheds.
6.7 Thickness of silicon rubber for core.
6.8 Creepage distance.
6.9 Protected creepage distance over silicone rubber  of complete insulator (90 deg. shadow).
6.10 Electric arcing Distance
6.11 Total length.
	mm

mm
mm
mm
mm



mm
mm
mm
	---------------

---------------

---------------

---------------

---------------

---------------

---------------

---------------


---------------

---------------

---------------
	---------------

---------------

---------------

---------------

---------------

---------------

---------------

---------------


---------------

---------------        

---------------

	7.
	Tests:

7.1 Comply with standard (IEC 61109 or ANSI C29.11).

7.2    Are Test reports attached?
	
Y/N
	---------------

---------------
	---------------

---------------

	8.
	Packing and shipping:

8.1 Net weight 

8.2 Standard package

8.3 Weight of crate

8.4 Package volume
	kg
kg
kg

m3
	---------------

---------------

---------------

---------------
	---------------

---------------

---------------

---------------

	9.
	Is silicone rubber  composite tension insulator moulded?
If not determine the method used for assembling sheds.
	Y/N
	---------------


---------------
	---------------


---------------

	10.
	Has an Ageing Test been performed in accordance with applicable IEC standards?

Duration of ageing test?

Name and Location of Testing Laboratories?
	
	
---------------

---------------

---------------
	
---------------

---------------

---------------

	11.
	Marking of Insulator?
	
	---------------
	---------------

	12.
	Is (ISO) certificate attached?
	Y/N
	---------------
	---------------

	13.
	Is Reference list attached?
	Y/N
	---------------
	---------------

	14.
	Has a 1,000 hour salt fog multi-stress test according to lEC 62217-2012 test been performed successfully? 
	Y/N
	---------------
	---------------

	15.
	No. of years the specified silicone rubber  composite tension insulator has been in production?
	Year
	---------------
	---------------

	16.
	Experience in silicone rubber  composite insulator manufacturing
	Year
	---------------
	---------------


SCHEDULE D1
DRAWINGS
[image: image1.jpg]


[image: image4.png]



[image: image2.emf]Technical Data:

1. Nominal System Voltage: 11 kV

2. Maximum Voltage: 12 kV

3. Impulse Withstand Voltage: 95 kV

4. Power Frequency Withstand Voltage: 38 kV

5. Short Circuit System Level: 25 kA.

6. Creepage Distance: 400 mm

7. Protected Creepage Distance:  160 mm

8. Tensile Strength: 80 kN

THE JORDANIAN ELECTRIC POWER CO. LTD

11 KV Silicon Composite Insulator

SCALE: DATE:  DRAWING NO.


SCHEDULE D1
DRAWINGS

[image: image3.emf]Technical Data:

1. Nominal System Voltage: 33 kV

2. Maximum Voltage: 36 kV

3. Impulse Withstand Voltage: 250 kV

4. Power Frequency Withstand Voltage: 95 kV

5. Short Circuit System Level: 31.5 kA.

6. Creepage Distance: 1089 mm

7. Protected Creepage Distance:  545 mm

8. Tensile Strength: 80 kN

THE JORDANIAN ELECTRIC POWER CO. LTD

33 KV Silicon Composite Insulator

SCALE: DATE:  DRAWING NO.


SCHEDULE D2
DRAWINGS and MAINTENANCE INSTRUCTIONS
All drawings shall be to scale and fully detailed.  All important dimensions shall be given and the material of which each part is to be constructed shall be indicated.

Drawings for approval shall be submitted in duplicate as paper prints and, after having approved, the Supplier shall supply any further copies required by the Engineer, one copy at least being a reproduction tracing cloth or approved plastic film. 

MAINTENANCE INSTRUCTIONS

Before the completion date for the first batch of post insulators the Contractor shall submit full Maintenance Instructions, and shall supply such further copies as may be required by the Engineer.

The following is a list of drawings which shall be submitted by the Tenderer with this offer:-

(a)
Detail drawings of insulators including electrical characteristics and creepage distances.

(b)
Drawings of all lables.

sCHEDULE E
STANDARDS
The Tenderer shall list the standard specifications to which the main items of tendered equipment are designed and manufactured.  

	Equipment
	National Standard
	English Title

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	


SCHEDULE F1
list of equipment with prices

To complete each equipment details in this schedule there shall be provided the necessary oil (synthetic liquid), cable boxes, all auxiliary apparatus, including any steelwork, panel wiring, fuses, interlocking gear, holding down bolts, screens, guards, labels, cable sockets, connectors and all necessary sundries whether specified in detail or not.  

SCHEDULE F1 - Continued
Silicone rubber  composite tension insulators
Item 1: 

12 kV, Silicone rubber  composite tension insulator complete with end fittings (Ball 16mm – Socket 16mm with stainless steel “W” clip) with the following electrical and mechanical features:

· System voltage.






12kV

· Impulse withstand voltage, 1.2/50 µs, positive.


95kV
· One minute power frequency withstand voltage, 50Hz, wet.
38kV
· Specified mechanical load SML, tension.



80kN
· Creepage distance.





400mm
· Protected creepage distance over silicone rubber  of 
             Complete insulator (90 deg. shadow).



160mm
· Routine test load.





32kN

· Color.







Gray 
· Total length                                                                                     ≤360mm

Item 2: 

36 kV, Silicone rubber  composite tension insulator complete with end fittings  (Ball 16mm – Socket 16mm with stainless steel “W” clip) with the following electrical and mechanical features:

· System voltage.






36kV

· Impulse withstand voltage, 1.2/50 µs, positive.


250kV
· One minute power frequency withstand voltage, 50Hz, wet.
95kV
· Specified mechanical load SML, tension.



80kN
· Creepage distance.





1089mm
· Protected creepage distance over silicone rubber  of 
complete insulator (90 deg. shadow).



545mm
· Routine test load.





32kN 
· Color







Gray

· Total lemgth                                                                                    ≤640mm

SCHEDULE F2
MANUFACTURERS AND 
Summary Schedule

Technical and Commercial Data

Note: The following schedule represents the most essential data based on which the evaluation process shall be performed.
	Item
	Description
	Quantity
	Manufacturer& Place of

Manufacture
	Place of Testing & Inspection
	Unit CFR to Aqaba Port Price/ Currency
	Total CFR to Aqaba Port Price/ Currency
	Delivery

(Weeks)

	1.
	12 kV, Silicone rubber composite tension insulator complete with end fitting (Ball 16mm – Socket 16mm with stainless steel “W” clip)
	1,000
	
	
	
	
	

	2.
	36 kV, Silicone rubber composite tension insulator complete with end fitting (Ball 16mm – Socket 16mm with stainless steel “W” clip)
	5,000
	
	
	
	
	


schedule G
deviations from specification
(a) It will be assumed that the plan offered will conform to the Specification in all respects unless deviations are mentioned in this Schedule.  

(b) The Purchaser may waive any minor informality, non-conformity or irregularity in an offer that does not constitute a material deviation provided such waiver does not prejudice or affect the ranking of any Tenderer.  Major deviations in the opinion of the Engineer will render the bid non‑responsive.  
(c) If, upon completing manufacturing and during inspection and delivery process, it is found that certain items that are required and clearly stated in the technical specifications but not included in the final product are not declared in the schedule of deviations (K), then the technical specifications shall prevail and the manufacturer shall be responsible for adding these items to fulfill all requirements called for in the specification at his own cost unless otherwise agreed with the Engineer.

schedule H
list of special tools and equipment required for maintenance purposes
List of Special Tools and Equipment to be provided by the Contractor for maintenance purposes and included in the bid price.  

schedule I
transport facilities
General
It shall be the responsibility of the Contractor to arrange for the shipment of all equipment from the country of origin to the Port of Entry in the Hashemite Kingdom of Jordan.  

Seafreight

When equipment is shipped by sea it must be consigned to the Port of Aqaba.  

Transfer of equipment from ship to shore is normally done by mobile crane or ships derricks, otherwise by lighters which have a maximum capacity of 500 tonnes.  Unloading from the lighter to the quay is limited to a maximum lift of 10 tonnes by means of a mobile crane.  

Roll-on and roll-off facilities are also available for containerized goods.  Containerized goods may be consigned to Amman for customs clearance.  

For special heavy loads a ‘Z’ craft is available in the harbour onto whica heavy trailer can be manoeuvred from a special base constructed for this purpose.  

Trailers with a loading capacity of up to 40 tonnes are available in Jordan and therefore the limit of weight which can be handled depends entirely on the capacity of the ships derricks.  

Transport from the Port normally is on 340 km of rough road although there is a rail head at Ma’an (100 km north of Aqaba).  The rail gauge is 1050 mm and the rail company possesses eighteen “flats” each with a maximum capacity of 15 tonnes.  

Airfreight

When airfreight of equipment is authorized it must be consigned to Queen Alia International Airport, Amman.  

Any goods to be shipped by air may be made by eligible airlines in accordance with Clause 1.4 of Instructions to Bidders.  The Jordanian International Airport is Amman’s Queen Alia International Airport (QAIA).  The Royal Jordanian airlines have direct services to this airport.  

schedule  J 

test certificateS and reference list

General
It shall be the responsibility of the Contractor to provide all test certificates and reference list for the required items with the submitted offer.

9. Total lemgth shall not exceed 360mm





9. Total lemgth shall not exceed 640mm








* 	Unless otherwise specified.


*	Materials and apparatus shall be tested at the Maker's Works in accordance with the appropriate National/International Specifications or equivalent specifications which may be applicable.





25
39

_1297149183.vsd
Technical Data:
1. Nominal System Voltage: 11 kV
2. Maximum Voltage: 12 kV
3. Impulse Withstand Voltage: 95 kV
4. Power Frequency Withstand Voltage: 38 kV
5. Short Circuit System Level: 25 kA.
6. Creepage Distance: 400 mm
7. Protected Creepage Distance:  160 mm
8. Tensile Strength: 80 kN


THE JORDANIAN ELECTRIC POWER CO. LTD


11 KV Silicon Composite Insulator


SCALE:


DATE: 


DRAWING NO.



_1297147927.vsd
Technical Data:
1. Nominal System Voltage: 33 kV
2. Maximum Voltage: 36 kV
3. Impulse Withstand Voltage: 250 kV
4. Power Frequency Withstand Voltage: 95 kV
5. Short Circuit System Level: 31.5 kA.
6. Creepage Distance: 1089 mm
7. Protected Creepage Distance:  545 mm
8. Tensile Strength: 80 kN


THE JORDANIAN ELECTRIC POWER CO. LTD


33 KV Silicon Composite Insulator


SCALE:


DATE: 


DRAWING NO.



